## cONTENT (hidden)
TABLE OF CONTENT
|  |  | Number of pages | From page | Until page | Page tbulate | PAGE
1 | DESIGN CODE & SPECIFICATION |  | 1 | 1 | 1 | 1 - 1 | 1
2 | SHELL DESIGN THICKNESS CALCULATION |  | 1 | 2 | 2 | 2 - 2 | 2
3 | BOTTOM PLATE, / ANNULAR &BOTTOM PLATE DESIGN |  | 1 | 3 | 3 | 3 - 3 | 3 | `
4 | ROOF THICKNESS CALCULATION |  | 1 | 4 | 4 | 4 - 4 | 4
5 | DESIGN OF ROOF-TO-SHELL JUNCTION - APPENDIX F |  | 1 | 5 | 5 | 5 - 5 | 5
6 | INTERMEDIATE WIND GIRDER DESIGN |  | 1 | 6 | 6 | 6 - 6 | 6
7 | WIND DESIGN & ANCHOR BOLT CALCULATION |  | 1 | 7 | 7 | 7 - 7 | 7
8 | WEIGHT CALCULATION |  | 1 | 8 | 8 | 8 - 8 | 8 |  | 1.0 DESIGN CODE & SPECIFICATION
9 | WEIGHT CALCULATION |  | 5 | 9 | 13 | 9 - 13 | 9 - 13
10 | TANK STABILITY AGAINST WIND LOADING |  | 5 | 14 | 18 | 14 - 18 | 14 - 18
11 | ` |  | 1 | 19 | 19 | 19 - 19 | 19
12 | SLING & WIRE ROPE CALC (SKID) |  | 1 | 20 | 20 | 20 - 20 | 20
APPENDIX
13 | COG CALCULATION FROM CADWORK |  | 3 | 21 | 23 | 21 - 23 | 21 - 23
14 | ALLOWABLE STRESS REFERENCE |  | 1 | 24 | 24 | 24 - 24 | 24
TANK STABILITY AGAINST WIND LOADING
Note on N4: nasrul: PLEASE UNHIDE TO SHOW PAGE FORMULA
PREVIEW
list

## cONTENT (2)
TABLE OF CONTENT
|  |  | Number of pages | From page | Until page | Page tbulate | PAGE
1 | DESIGN CODE & SPECIFICATION |  | 1 | 1 | 1 | 1 - 1 | 1
2 | SHELL DESIGN THICKNESS CALCULATION |  | 1 | 2 | 2 | 2 - 2 | 2
3 | BOTTOM PLATE, / ANNULAR &BOTTOM PLATE DESIGN |  | 1 | 3 | 3 | 3 - 3 | 3 | `
4 | INTERMEDIATE WIND GIRDER DESIGN |  | 1 | 4 | 4 | 4 - 4 | 4
5 | WIND DESIGN & ANCHOR BOLT CALCULATION |  | 2 | 5 | 6 | 5 - 6 | 5 - 6
6 | WEIGHT CALCULATION |  | 2 | 7 | 8 | 7 - 8 | 7 - 8
7 | WEIGHT CALCULATION |  | 1 | 9 | 9 | 9 - 9 | 9
8 | WEIGHT CALCULATION |  | 1 | 10 | 10 | 10 - 10 | 10 |  | 1.0 DESIGN CODE & SPECIFICATION
9 | WEIGHT CALCULATION |  | 5 | 11 | 15 | 11 - 15 | 11 - 15
10 | TANK STABILITY AGAINST WIND LOADING |  | 5 | 16 | 20 | 16 - 20 | 16 - 20
11 | ` |  | 1 | 21 | 21 | 21 - 21 | 21
12 | SLING & WIRE ROPE CALC (SKID) |  | 1 | 22 | 22 | 22 - 22 | 22
APPENDIX
13 | COG CALCULATION FROM CADWORK |  | 3 | 23 | 25 | 23 - 25 | 23 - 25
14 | ALLOWABLE STRESS REFERENCE |  | 1 | 26 | 26 | 26 - 26 | 26
TANK STABILITY AGAINST WIND LOADING
Note on N4: nasrul: PLEASE UNHIDE TO SHOW PAGE FORMULA
PREVIEW
list

## WATER_SS_TANK (hidden)
| STORAGE TANK DESIGN CALCULATIONS | [9 empty] | YELLOW | BLUE
[11 empty] | INPUT | CALC
1.0 | DESIGN CODE & SPECIFICATION
[8 empty] | : | API 650 |  |  |  | LIM CHAN LIAN
1.1 | TANK
| Service | [6 empty] | : | Water Tank |  |  |  | 12:38 PM (5 hours ago)
| Item number | [6 empty] | : | -
| Type of tank | [6 empty] | : | Self Supported |  |  |  | to me
[9 empty] | Cone Roof |  |  |  | Hi Sir,
1.2 | GEOMETRIC DATA
| Outside diameter , Do |  |  |  |  | 17.2244 | ft | = | 5250 | mm |  |  | New Tank Specification
| Tank height , H |  |  |  |  | 37.7295 | ft | = | 11500 | mm |  |  | Product: Waste water, Oily based.
| Specific gravity of operating liquid , S.G. | [6 empty] | = | 1 |  |  |  | New Tank Diameter: 5,250mm O/D x 11,500mm S/L
| Nominal capacity , M | [6 empty] | = | 249.0469 | m³ |  |  | Top Section: Cone with bracing ribs
| Maximum design liquid level, HL | [6 empty] | = | 10000 | mm |  |  | Bottom Section: Flat bottom
Material: AISI 304L
1.3 | PRESSURE & TEMPERATURE | [11 empty] | Finishing: 2B Milled
| Design pressure |  |  | : Upper , PU = |  | 8500 | mm H2O | = | 833.85 | mbar.g. |  |  | Welding: Argon TIG/ Arc welding. Acid pickled and cleaned.
|  |  |  | : Lower , PL = |  | 0 | mm H2O | = | 0 | mbarg.Vac
| Design temperature |  |  | : Upper , TU |  |  |  | = | 60 | °C |  |  | Fitment : Top Open
1.4 | MATERIAL & MECHANICAL PROPERTIES | [11 empty] | Bottom base plate 6mm thickness
Lowest bottom 2 courses 5mm thick x 4.5m height
| Component | Material |  | Tensile Stress |  | Yield Stress |  | Corr. Allow. |  |  |  |  | Second 2 courses 4mm thick x 4.5m height
|  |  |  | St (N/mm²) |  | Sy (N/mm²) |  | c.a.(mm) |  |  |  |  | Top course 3mm thick x 3.0m height
| PLATE | [11 empty] | Ring inforcement - Rolled angle bar 6mm x 75mm on 6 courses
| Shell Plate | A 304L |  | 485 |  | 170 |  | 0
| Bottom Plate | A 304L |  | 485 |  | 170 |  | 0 |  |  |  |  | Bottom outlet, 2no. 6" and 4" Flange (1 spare)
| Roof Plate | A 304L |  | 485 |  | 170 |  | 0 |  |  |  |  | Bottom side agitator, reuse motor, please check motor RPM (review on-site by contractor)
| Stiffener Ring | A 304L |  | 485 |  | 170 |  | 0
| STRUCTURE | [11 empty] | Bottom side manhole SS304 800mm (New)
| Top Curb Angle | A 304L |  | 485 |  | 170 |  | 0
Design for thickness and support bracing by contractor. Contractor to design out the tank strength based on the product spec.
2.0 | SHELL DESIGN THICKNESS CALCULATION | [11 empty] | No longer needed
2.1 | GEOMETRIC DATA | [11 empty] | a. Middle manhole
| Plate width used |  |  |  |  | 54.1339 | ft | : | 16500 | mm
| Plate height |  |  |  |  | 5 | ft | : | 1524 | mm |  |  | Contractor must ensure tank workmanship and no leakage. Warranty of one year shall be given for manufacturing defect. Leaks test shall be performed.
2.2 | MATERIAL & MECHANICAL PROPERTIES
| Material used | [6 empty] | : | A 304L | [5 empty] | 37.7295
| Specified minimum tensile stress, Ss | [6 empty] | = | 485 | N/mm²
| Specified minimum yield stress, Sy | [6 empty] | = | 170 | N/mm²
| Yield strength reduction factor, k ( Appendix M ) | [6 empty] | = | 1
| Joint Efficiency, E | [6 empty] | = | 0.85
| Max.allowable design stress,Sd | [6 empty] | = | 113.3333 | N/mm²
| Max.allowable hydro. test stress,St | [6 empty] | = | 127.5 | N/mm²
(As per Table 3-2 )
2.3 | SPECIFIED MINIMUM SHELL THICKNESS
| Specification | [6 empty] | : | API 650 Clause 3.6.1
| Minimum thickness | [7 empty] | 5 | mm
2.3 | TANK SHELL THICKNESS CALCULATION | [14 empty] | By one foot method. See sec. 3.6.3.2
|  | D | = Inside diameter of tank |  |  |  |  | = | 17.2244 | ft | [5 empty] | on page 3-7 of API - 650
|  | H | = Design liquid level |  |  |  |  | = | 37.7295 | ft |  |  | Course # | Liq. height | Height of | Design shell | Design shell | Hyd. shell | Adopted shell | Selected Min.
|  | Hi | = Internal design pressure |  |  |  |  | = | 27.8871 | ft. water |  |  | from bottom | in tank | each Course | thickness | thickness | thickness | thickness | shell thickness
|  | G | = Specific gravity of liquid |  |  |  |  | = | 1 |  |  |  | of tank | (H) |  | (td) | (td) | (tt)
|  | c.a. | = corrosion allowance |  |  |  |  | = | 0 | in |  |  |  | ft | mm | inches | mm | inches | (mm) | (mm)
|  | Sd | = Allow. stress for design condition |  |  |  |  | = | 16437.64 | psi
|  | St | = Allow. stress for hydrostatic test condition |  |  |  |  | = | 18492.345 | psi |  |  | 1 | 37.7295 | 1524000 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7
| Shell Thk at design condition (td) = | [9 empty] | td = 2.6(D)(H -1)(G)/(E*Sd) + ca |  |  | -4960.9905 | 1524000 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7
| Shell Thk at hydrotest condition (tt) = | [9 empty] | tt = 2.6(D)(H -1)(G)/St + ca
2.4 | CALCULATION & RESULTS | [11 empty] | 3 | -9959.7105 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7
[13 empty] | 4 | -9959.7105 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7
| Course # | Liquid | Liquid | Height of | t.design | t.hydro. | t.used | [5 empty] | 5 | -9959.7105 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7
| from bottom | height | height | each | (td) | (tt) | (t) |  | RESULTS
| bottom | (H) | (H) | Course
| of tank | mm | ft | mm | (mm) | (mm) | (mm) | [5 empty] | 6 | -9959.7105 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7
[13 empty] | 7 | -9959.7105 | -3036497.0899 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 7
| 1 | 11499.9653 | 37.7295 | 1524 | 3.3973 | 3.0198 | 5 | = | O.K. |  | 37.7295
| 2 | 9975.9653 | 32.7295 | 1524 | 2.9903 | 2.658 | 5 | = | O.K. |  | 11499.9653
| 3 | 8451.9653 | 27.7295 | 1524 | 2.5832 | 2.2962 | 5 | = | O.K.
| 4 | 6927.9653 | 22.7295 | 1524 | 2.1761 | 1.9343 | 4 | = | O.K.
| 5 | 5403.9653 | 17.7295 | 1524 | 1.7691 | 1.5725 | 4 | = | O.K.
| 6 | 3879.9653 | 12.7295 | 1524 | 1.362 | 1.2107 | 4 | = | O.K.
| 7 | 2355.9653 | 7.7295 | 1524 | 0.95494 | 0.84883 | 3 | = | O.K.
| 8 | 831.9653 | 2.7295 | 1524 | 0.54787 | 0.487 | 3 | = | O.K.
=
=
=
[8 empty] | = | [5 empty] | Course # | Liq. height | Height of
[8 empty] | = | [5 empty] | from bottom | in tank | each Course
[14 empty] | of tank | (H)
| By one foot method. See sec. 3.6.3.2 | [13 empty] | ft | mm
By one foot method. See sec. 3.6.3.2
| on page 3-7 of API - 650 | [9 empty] | Note: | According to sec. 3.6.1.1 min. thk.of tank of dia. 50ft to <120ft should be 1/4 inches.
3.0 | BOTTOM PLATE DESIGN
3.1 | Minimum thickness as per |  |  |  | API 650 Clause 3.4.1 |  |  | = | 6 | mm
| Corrosion allowance , c.a. | [6 empty] | = | 0 | mm
| Minimum thickness required | [6 empty] | = | 6 | mm
| Therefore, use thickness of |  |  |  | 6 | mm (tb) is | satisfactory.
3.2 | ANNULAR BOTTOM PLATE DESIGN:
3.3 | As per API 650 Add. 2 Sect. 5.11.2;
| Minimum Annular plate Width shall be = |  |  |  | 215 tb |  |  |  | 380.4002 | mm
(GH)^0.5
[6 empty] | or a Minimum of |  |  | 600 | mm
| Annular Plate width provided | [7 empty] | 700 | mm
| Where: | tb = Annular plate thickness, mm
H = maximum Design Liquid level, Meter
|  | G = liquid Specific gravity |  |  |  |  | Therefore |  | satisfactory.
4.0 | MINIMUM ROOF THICKNESS
4.1 | Minimum thickness as per |  |  |  | API 650 Clause 3.10.2 |  |  | = | 4.7 | mm |  | ANNULAR BOTTOM PLATE DESIGN:
| Corrosion allowance, c.a. | [6 empty] | = | 0 | mm |  | As per API 650 11th Ed. 2009 Add. 2 Sect. 5.5.2;
| Minimum thickness required | [6 empty] | = | 4.7 | mm |  | Minimum Annular plate Width shall be = |  |  | 215 tb |  | 28.62 | 727 | mm
| Therefore , use thickness of |  |  |  | 5 | mm is | satisfactory. | [7 empty] | ( GH )0.5
[16 empty] | or a Minimum of | 23.622 | 600 | mm
4.2 | SELF SUPPORTED CONE ROOF
| (1) Minimum thickness shall be the greater of the followings (a) and (b) :- | [10 empty] | Annular Plate width provided; in |  |  |  |  | 29.92 | 760 | mm
| (a) Minimum thickness as per |  |  |  | API 650 Clause 3.10.2 |  |  | = | 4.7625 | mm | [5 empty] | Where: tb = Annular plate thickness, mm
| (b) Minimum thickness, ( clause 3.10.6.1 ) | [14 empty] | H = maximum Design Liquid level, Meter
|  |  | Di | [12 empty] | G = liquid Specific gravity
|  | tmin | = |  |  |  |  | = | 4.2259 | mm
|  |  | 400 sin ß° | [8 empty] | HENCE, OK.
|  | ß° | = Roof slope |  |  |  |  | = | 15 | °
| Minimum thickness required (max. of (a) & (b)) | [6 empty] | = | 4.7625 | mm
4.3 | CHECK FOR ROOF LOADING
| Roof plate weight , @ assume Roof thk = |  |  |  |  | 5 | mm,wr | = | 0.00038504 | N/mm²
| Vacuum pressure , Va | [6 empty] | = | 0 | N/mm²
| Uniform live load , wl |  |  |  | @ | 25 | lbs/ft² | = | 0.0011962 | N/mm²
| Add. live load exceeding 122 kg/m², wa @ |  |  |  |  | 0 | lbs/ft² | = | 0 | N/mm²
| Total live load plus dead loads, wld | [6 empty] | = | 0.0015812 | N/mm²
[8 empty] | = | 33.0473 | lbs/ft²
[8 empty] | < | 45 | lbs/ft²
| The roof plate shall be increased by the following ratio , k | [6 empty] | = | 1
| Minimum thickness required, tmin | [6 empty] | = | 4.7625 | mm
| Corrosion allowance, c.a. | [6 empty] | = | 0 | mm
| Therefore, minimum thickness ( + corrosion allowance ) | [6 empty] | = | 4.7625 | mm
| (2) Maximum thickness | [6 empty] | = | 6 | mm
| Therefore , use thickness of |  |  |  | 5 | mm is | satisfactory.
5.0 | DESIGN OF ROOF-TO-SHELL JUNCTION - APPENDIX F
| Roof thickness, tr | [6 empty] | = | 5 | mm
| Roof slope, ß ( 9.5° < ß < 37° ) | [6 empty] | = | 15 | °
| Top curb angle used | [6 empty] | : | L 75 x 75 x 6 |  | 6mm x 75mm on 6
| Unit weight , wtca | [6 empty] | = | 5.91 | kg/m
| Leg length, L | [6 empty] | = | 75 | mm
| Leg thickness, t ( corroded ) | [6 empty] | = | 6 | mm
| Section modulus, Za ( corroded ) | [6 empty] | = | 7100 | mm³
| Cross sectional area of angle , A ( corroded ) | [6 empty] | = | 703 | mm²
| Wh = | lesser of [ 0.3 R2.th ] or [ 304.8 mm ]
|  | = | 67.5574 | mm |  |  | th =
[7 empty] | 5 | mm
|  |  | 6 | mm
t =
|  |  | Wc.min = | 75 |  | R2 = | Rc / sinß
|  |  |  | mm |  | = | 10142.2212 | mm
[6 empty] | Rc = | 2625 | mm
|  | Wc = | 0.6 Rc.tt.corr
|  | = | 75 | mm |  | tt.corr = | 3 | mm
Total shaded area resisting the compressive force,
|  | Aa | = Wh.th + Wc.tt.corr + A |  |  |  |  | = | 1265.7869 | mm²
5.1 | MINIMUM REQUIRED COMPRESSION AREA AT THE ROOF TO SHELL JUNCTION
D²
|  | Ar | = |  |  |  |  | = | 246.5123 | mm²
3000.sin ß°
where
|  | D | = Nominal tank diameter |  |  |  |  | = | 17.2244 | ft
|  | Since Ar | < | Aa, therefore it is |  | satisfactory.
5.2 | CHECK FOR MAXIMUM DESIGN PRESSURE
|  |  | 0.245.W |  | 0.735.M
| P.max |  | = | + 8.th - |  |  |  | = | 715.8431 | mbar
|  |  | D² |  | D³
where
| W |  | =Total weight of shell and any framing(not roof plates) |  |  |  |  | = | 345980 | lbs
supported by the shell & roof
| th |  | = Roof plate thickness |  |  |  |  | = | 0.19685 | in
| M |  | = Wind moment |  |  |  |  | = | 2.1945 | lbs.ft
| Since Pi |  | > | P, therefore it is |  | not satisfactory !!!
6.0 | INTERMEDIATE WIND GIRDER DESIGN
6.1 | Maximum Height Of The Unstiffened Shell
|  |  |  | 100tt.corr ³ |  | 100 ²
|  | H1 | = 6(100tt.corr) |  | x | x k |  | = | 12659.475 | mm
|  |  |  | D |  | V
where
|  | tt.corr | = Thickness of the top shell course (corroded) |  |  |  |  | = | 0.11811 | in | 3
|  | D | = Nominal tank diameter |  |  |  |  | = | 17.2244 | ft
|  | V | = Wind design speed ( @ |  |  | 44 | m/s ) | = | 98.4298 | miles/hr
|  | k | = Yield strength reduction factor ( Appendix M ) |  |  |  |  | = | 1
6.2 | Location Of Intermediate Wind Girder
| Course |  | Thickness. |  | Actual Width |  | Transposed Width
|  |  | t.corr |  | W |  | Wtr =W(tt.corr / t.corr)^2.5
|  |  | (mm) |  | (mm) |  | (mm)
| 1 (bottom) |  | 5 |  | 16500 |  | 4601.1042
| 2 |  | 5 |  | 16500 |  | 4601.1042
| 3 |  | 5 |  | 16500 |  | 4601.1042
| 4 |  | 4 |  | 16500 |  | 8037.7983
| 5 |  | 4 |  | 16500 |  | 8037.7983
| 6 |  | 4 |  | 16500 |  | 8037.7983
| 7 |  | 3 |  | 16500 |  | 16500
| 8 |  | 3 |  | 16500 |  | 16500
|  |  | 0 |  |  |  | #DIV/0!
|  |  | 0 |  |  |  | #DIV/0!
|  |  | #VALUE! |  |  |  | #VALUE!
|  |  | #VALUE! |  |  |  | #VALUE!
|  |  | 0 |  |  |  | #DIV/0!
|  |  | 0 |  |  |  | #DIV/0!
|  |  | #VALUE! |  |  |  | #VALUE!
|  |  |  | Height of transformed shell, H2 = |  |  | 70916.7075
REMARK : Let all 'Wtr' equal to zero for 'negative' t.corr
|  | Since H1 | < | H2 , therefore an intermediate wind girder is |  |  |  |  | required. |  |  |  |  | VERIFICATION OF UNSTIFFENED SHELL FOR EXTERNAL PRESSURE
| No of Wind Girder required |  |  | = |  | H2 / H1 |  | = | 6
| THEREFORE , NO OF WIND GIRDER REQUIRED | [6 empty] | = | 6
| LOCATION EQUA SPACED OF STIFFENER RING | [6 empty] | = | 1916.6667
Need not to be evaluated as the design external pressure is zero. As per Chapter 3, Clause 3.2.1.i, design external
7.0 | WIND DESIGN CALCULATION | [12 empty] | pressure shall not be less than 0.25 kPa. The tanks designed as per API 650 can sustain this minimum pressure.
| Design code | [6 empty] | : | ASCE -7
7.1 | GEOMETRIC DATA
| Internal design pressure, |  |  | Pi @ | 833.85 | mbar |  | = | 0.083385 | N/mm²
| Diameter of tank, Di | [6 empty] | = | 0.056511 | mm
| Tank height , Hs | [6 empty] | = | 11500 | mm
| Roof slope, ß° | [6 empty] | = | 15 | °
| Roof height, Hr | [6 empty] | = | 0.007571 | mm
| Height from tank bottom to shell centre, Ls | [6 empty] | = | 5750 | mm
| Height from tank bottom to roof centre,Lr | [6 empty] | = | 11500.0025 | mm
| Min. depth of product ( always present in tank) , Hw | [6 empty] | = | 50 | mm
| Weight of tank,Wt |  | (@ | 10037.9336 | kg) |  |  | = | 98472.129 | N
| Weight of product ( always present in tank) , Ww | [6 empty] | = | 1.2302e-06 | N
7.2 | WIND FORCE CALCULATIONS
The wind loading shall be determined as follows : -
|  | H | = P.A.C.I | N
where
|  | P | = Wind dynamic pressure ( N/m² ) |  |  |  |  | = | 900
|  | Cr | = Shape factor for roof |  |  |  |  | = | 0.75
|  | Cs | = Shape factor for shell |  |  |  |  | = | 0.75
|  | Ar | = Projected area of roof ( = 0.5.Di.Hr ) |  |  |  |  | = | 2.1392e-10 | m²
|  | As | = Projected area of shell ( = Di.Hs ) |  |  |  |  | = | 0.00064987 | m²
|  | I | = Appurtenances |  |  |  |  | = | 1.18
| Total wind load exerted on roof, Fr | [6 empty] | = | 1.7039e-07 | N
| Total wind load exerted on shell, Fs | [6 empty] | = | 0.51762 | N
| Total wind moment on tank, Mwind ( = Fr.Lr + Fs.Ls ) | [6 empty] | = | 2976.3303 | Nmm
7.3 | TANK STABILITY AGAINST WIND LOADING
7.3.1 | CASE 1 - EMPTY CONDITION
Resistance to overturning moment,
|  | Mres. | = 0.5Di.( Wt - 0.25 p Di².Pi ) |  |  |  |  | = | 2782.3561 | Nmm
| Safety factor, Sa ( = Mres./Mwind ) | [6 empty] | = | 0.93483
[8 empty] | < | 1.5
|  | Since Sa | < | 1.5, therefore the tank is structurally
|  | unstable. | Tank anchorage is |  | required for this case !!!
7.3.2 | CASE 2 - OPERATING CONDITION
Resistance to overturning moment,
|  | Mres. | = 0.5Di.( Wt + Ww - 0.25 p Di².Pi ) |  |  |  |  | = | 2782.3561 | Nmm
| Safety factor, Sa ( = Mres./Mwind ) | [6 empty] | = | 0.93483
[8 empty] | < | 1.5
|  | Since Sa | < | 1.5, therefore the tank is structurally
|  | unstable. | Tank anchorage is |  | required for this case !!!
7.4 | ANCHOR BOLT DESIGN
7.4.1 | GEOMETRIC DATA
| Number of bolts , N | [6 empty] | = | 35
| Diameter of anchor bolt, d | [6 empty] | = | 30 | mm
| Diameter of anchor bolt, d.corr ( less c.a.@ |  |  |  |  | 0 | mm) | = | 30 | mm
| Bolts circle diameter, Da | [6 empty] | = | 5370 | mm
| Root area of each hold down bolt, Ab | [6 empty] | = | 706.8583 | mm²
| Spacing between anchor bolts, Sb | [6 empty] | = | 482.0101 | mm
7.4.2 | BOLT MECHANICAL PROPERTIES
| Allowable stress, St.all | [6 empty] | = | 103 | N/mm²
7.4.3 | ANCHOR BOLTS DESIGN
Tensile force,
|  |  | 1 4.Mwind |  | Pi. pDi²
|  | T = |  | - Wt - |  |  |  | = | -2813.4261 | N
N Da 4
Tensile stress,
T
|  | sb | = |  |  |  |  | = | -3.9802 | N/mm²
Ab
|  | Since sb | < | St.all, therefore the anchor bolt size is |  |  |  | satisfactory.
8.0 | WEIGHT CALCULATION
8.1 | General
|  | Design code | [5 empty] | : | API 650
|  | Service | [5 empty] | : | Water Tank
|  | Item number | [5 empty] | : | -
|  | Type of tank | [5 empty] | : | Self Supported
Cone Roof
|  | Inside diameter, Di | [5 empty] | = | 5250 | mm
|  | Tank height, H | [5 empty] | = | 11500 | mm
|  | Density of steel | [5 empty] | = | 8000 | kg/m³
8.2 | ERECTION WEIGHT
8.2.1 | Weight of bottom plate
|  | Material | [5 empty] | : | A 304L
|  | Diameter of bottom plate | [5 empty] | = | 5300 | mm
|  | Bottom plate thickness | [5 empty] | = | 6 | mm
|  | Weight of bottom plate | [5 empty] | = | 1058.9681 | kg
8.2.2 | Weight of shell
| Course | Material |  | Height | Length | Thickness | weight
| No. |  |  | (mm) | (mm) | (mm) | (kg)
| 1 (bottom) | A 304L |  | 1524 | 16500 | 5 | 1005.84
| 2 | A 304L |  | 1524 | 16500 | 5 | 1005.84
| 3 | A 304L |  | 1524 | 16500 | 5 | 1005.84
| 4 | A 304L |  | 1524 | 16500 | 4 | 804.672
| 5 | A 304L |  | 1524 | 16500 | 4 | 804.672
| 6 | A 304L |  | 1524 | 16500 | 4 | 804.672
| 7 | A 304L |  | 1524 | 16500 | 4 | 804.672
| 8 | A 304L |  | 1524 | 16500 | 4 | 804.672
| 9 | A 304L |  | 0 | 16500 | 4 | 0
| 10 | A 304L |  | 0 | 16500 | 4 | 0
| 11 | A 304L |  | 0 | 16500 | 4 | 0
[6 empty] | Total weight of shell |  | = | 7040.88 | kg
8.2.3 | Weight of roof plate
|  | Material | [5 empty] | : | A 304L
|  | Roof plate thickness, tr | [5 empty] | = | 5 | mm
|  | Length of slope | [5 empty] | = | 2717.6 | mm
|  | Area of roof plate | [5 empty] | = | 23201760.099 | mm²
|  | Weight of roof plate | [5 empty] | = | 928.0704 | kg
8.2.4 | Weight of top curb angle
|  | Material | [5 empty] | : | A 304L
|  | Angle size | [5 empty] | : | L 75 x 75 x 6
|  | Length of top curb angle | [5 empty] | = | 16493.3614 | mm
|  | Unit weight, wtca | [5 empty] | = | 5.91 | kg/m
|  | Weight of top curb angle | [5 empty] | = | 97.4758 | kg
|  | Total Erection Weight, We @ ( |  |  | 10 | % additional weight ) |  | = | 10037.9336 | kg
8.3 | OPERATING WEIGHT
8.3.1 | Weight of liquid
|  | Specific gravity of liquid | [5 empty] | = | 1
|  | Maximum design liquid level | [5 empty] | = | 10000 | mm
|  | Volume of liquid in tank | [5 empty] | = | 216.4754 | m³
|  | Weight of liquid, Wliq. | [5 empty] | = | 216475.3688 | kg
|  | Total operating weight , Wo ( = We + Wliq. ) | [5 empty] | = | 226513.3024 | kg
8.4 | HYDROSTATIC TEST WEIGHT
8.4.1 | Weight of water
|  | Specific gravity of water | [5 empty] | = | 1
|  | Height of water | [5 empty] | = | 11500 | mm
|  | Volume of water in tank | [5 empty] | = | 248.9467 | m³
|  | Weight of water, Wh2o | [5 empty] | = | 248946.6741 | kg
|  | Total hydrostatics test weight , Wh ( = We + Wh2o ) | [5 empty] | = | 258984.6077 | kg
TABLE SHOWN BELOW ONLY FOR INFORMATION WHILE DOING THE LIFTING LUG CALCULATION!!
(HIDE THE TABLE WHEN PRINTING !!!)
1. | WEIGHT OF BOTTOM PLATE (+ % of increased weight) | [6 empty] | = | 12466.1719 | N
2. | WEIGHT OF SHELL (+ % of increased weight) | [6 empty] | = | 82885.2394 | N
3. | WEIGHT OF ROOF PLATE (+ % of increased weight) | [6 empty] | = | 12072.7295 | N
[9 empty] | 107424.1408 | N
4. | TOTAL ERECTION WEIGHT |  |  |  | = | 10037.9336 | kg |  | 98472.129 | N
Sd
St

## API650-DESIGN CALCULATION
| STORAGE TANK DESIGN CALCULATIONS | [9 empty] | YELLOW | BLUE
[11 empty] | INPUT | CALC
1.0 | DESIGN CODE & SPECIFICATION
[8 empty] | : | API 650
1.1 | TANK
| Service | [6 empty] | : | Storage Tank
| Item number | [6 empty] | : | -
| Type of tank | [6 empty] | : | Self Supported
Cone Roof
1.2 | GEOMETRIC DATA
| Outside diameter , Do |  |  |  |  | 7.2178 | ft | = | 2200 | mm
| Tank height , H |  |  |  |  | 9.9278 | ft | = | 3026 | mm
| Specific gravity of operating liquid , S.G. | [6 empty] | = | 1
| Nominal capacity , M | [6 empty] | = | 11.5074 | m³ |  |  | We have a project awarded and need your strength calculation and GA drawing and details drawing.
| Maximum design liquid level, HL | [6 empty] | = | 3026 | mm
This tank need to be design under API 650 and we have not given much information about this tank, we assume design temperature is 40 DegC and the pressure is atmospheric pressure.
1.3 | PRESSURE & TEMPERATURE
| Design pressure |  |  | : Upper , PU = |  | 3026 | mm H2O | = | 296.8506 | mbar.g. |  |  | OD2200
|  |  |  | : Lower , PL = |  | 0 | mm H2O | = | 0 | mbarg.Vac |  |  | From top to bottom height is 3500
| Design temperature |  |  | : Upper , TU |  |  |  | = | 40 | °C
Major material has been procured –
1.4 | MATERIAL & MECHANICAL PROPERTIES | [11 empty] | Head 6mmT
Body 5mmT x 1524mmW
| Component | Material |  | Tensile Stress |  | Yield Stress |  | Corr. Allow. |  |  |  |  | Bottom Plate 8mmT
|  |  |  | St (N/mm²) |  | Sy (N/mm²) |  | c.a.(mm) |  |  |  |  | Ladder Rung 16mmD
PLATE
| Shell Plate | A 304 |  | 485 |  | 170 |  | 0 |  |  |  |  | Please quote us the best price for the job scope mentioned and you may contact me for details.
| Bottom Plate | A 304 |  | 485 |  | 170 |  | 0
| Roof Plate | A 304L |  | 485 |  | 170 |  | 0
2.0 | SHELL DESIGN THICKNESS CALCULATION
2.1 | GEOMETRIC DATA
| Plate width used |  |  |  |  | 22.6847 | ft | : | 6914.2857 | mm
| Plate height |  |  |  |  | 5 | ft | : | 1524 | mm
2.2 | MATERIAL & MECHANICAL PROPERTIES
| Material used | [6 empty] | : | A 304
| Specified minimum tensile stress, Ss | [6 empty] | = | 485 | N/mm²
| Specified minimum yield stress, Sy | [6 empty] | = | 170 | N/mm²
| Yield strength reduction factor, k ( Appendix M ) | [6 empty] | = | 1
| Joint Efficiency, E | [6 empty] | = | 0.85
| Max.allowable design stress,Sd | [6 empty] | = | 113.3333 | N/mm²
| Max.allowable hydro. test stress,St | [6 empty] | = | 127.5 | N/mm²
(As per Table 3-2 )
2.3 | SPECIFIED MINIMUM SHELL THICKNESS
| Specification | [6 empty] | : | API 650 Clause 3.6.1
| Minimum thickness | [7 empty] | 5 | mm
2.3 | TANK SHELL THICKNESS CALCULATION | [14 empty] | By one foot method. See sec. 3.6.3.2
| D | = Inside diameter of tank |  |  |  | 2190 | mm | = | 7.185 | ft | [5 empty] | on page 3-7 of API - 650
| H | = Design liquid level |  |  |  | 3026.0008 | mm | = | 9.9278 | ft |  |  | Course # | Liq. height | Height of | Design shell | Design shell | Hyd. shell | Adopted shell | Selected Min.
| Hi | = Internal design pressure |  |  |  | 3026.0099 | mm | = | 9.9278 | ft. water |  |  | from bottom | in tank | each Course | thickness | thickness | thickness | thickness | shell thickness
| G | = Specific gravity of liquid | [5 empty] | = | 1 |  |  |  | of tank | (H) |  | (td) | (td) | (tt)
| c.a. | = corrosion allowance |  |  |  | 0 | mm | = | 0 | in |  |  |  | ft | mm | inches | mm | inches | (mm) | (mm)
| Sd | = Allow. stress for design condition |  |  |  | 113.3333 | N/mm² | = | 16437.64 | psi
| St | = Allow. stress for hydrostatic test condition |  |  |  | 127.5 | N/mm² | = | 18492.345 | psi |  |  | 1 | 0 | 1524000 | #DIV/0! | #DIV/0! | #REF! | #DIV/0! | 7
| Shell Thk at design condition (td) = | [9 empty] | td = 2.6(D)(H -1)(G)/(E*Sd) + ca |  |  | -4998.72 | 1524000 | #DIV/0! | #DIV/0! | #REF! | #DIV/0! | 7
| Shell Thk at hydrotest condition (tt) = | [9 empty] | tt = 2.6(D)(H -1)(G)/St + ca
2.4 | CALCULATION & RESULTS | [11 empty] | 3 | -9997.44 | #REF! | #DIV/0! | #DIV/0! | #REF! | #DIV/0! | 7
[13 empty] | 4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7
| Course # | Liquid | Liquid | Height of | t.design | t.hydro. | t.used | [5 empty] | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7
| from bottom | height | height | each | (td) | (tt) | (t) |  | RESULTS
| bottom | (H) | (H) | Course
| of tank | mm | ft | mm | (mm) | (mm) | (mm) | [5 empty] | 6 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7
[13 empty] | 7 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 7
| 1 | 3025.9909 | 9.9278 | 1524 | 0.473 | 0.42044 | 5 | = | O.K. |  | 9.9278
| 2 | 1501.9909 | 4.9278 | 1524 | 0.30319 | 0.26951 | 5 | = | O.K. |  | 3025.9909
| 3 | -22.0091 | -0.072208 | 1524 | 0.13339 | 0.11857 | 5 | = | O.K.
| 4 | -1546.0091 | -5.0722 | 1524 | -0.036413 | -0.032367 | 4 | = | O.K.
| 5 | -3070.0091 | -10.0722 | 1524 | -0.20622 | -0.1833 | 4 | = | O.K.
| 6 | -4594.0091 | -15.0722 | 1524 | -0.37602 | -0.33424 | 4 | = | O.K.
| 7 | -6118.0091 | -20.0722 | 1524 | -0.54582 | -0.48518 | 3 | = | O.K.
| 8 | -7642.0091 | -25.0722 | 1524 | -0.71563 | -0.63611 | 3 | = | O.K.
=
=
=
[8 empty] | = | [5 empty] | Course # | Liq. height | Height of
[8 empty] | = | [5 empty] | from bottom | in tank | each Course
[14 empty] | of tank | (H)
| By one foot method. See sec. 3.6.3.2 | [13 empty] | ft | mm
By one foot method. See sec. 3.6.3.2
| on page 3-7 of API - 650 | [9 empty] | Note: | According to sec. 3.6.1.1 min. thk.of tank of dia. 50ft to <120ft should be 1/4 inches.
3.0 | BOTTOM PLATE DESIGN
3.1 | Minimum thickness as per |  |  |  | API 650 Clause 3.4.1 |  |  | = | 6 | mm
| Corrosion allowance , c.a. | [6 empty] | = | 0 | mm
| Minimum thickness required | [6 empty] | = | 6 | mm
| Therefore, use thickness of |  |  |  | 8 | mm (tb) is | satisfactory.
3.2 | ANNULAR BOTTOM PLATE DESIGN:
3.3 | As per API 650 Add. 2 Sect. 5.11.2;
| Minimum Annular plate Width shall be = |  |  |  | 215 tb |  |  |  | 988.767 | mm
(GH)^0.5
[6 empty] | or a Minimum of |  |  | 600 | mm
| Annular Plate width provided | [7 empty] | 700 | mm
| Where: | tb = Annular plate thickness, mm
H = maximum Design Liquid level, Meter
G = liquid Specific gravity
[5 empty] | Therefore, Bottom plate thickness |  |  | = | satisfactory.
4.0 | S.E. HEAD CALCULATION |  |  | UG-32 (d)
| Internal Design Pressure | [5 empty] | P | = | 0.00296 | Mpa
| Specific Gravity Internals | [5 empty] | g | = | 1 | mm
| Liquid/ Packing Head Pressure | [5 empty] | Ph | = | 0.00428 | Mpa
| Design Pressure Including Head | [5 empty] | P | = | 0.00724 | Mpa
| Design Temperature for Internal Pressure | [6 empty] | = | 40 | oC
| Internal Corrosion Allowance | [5 empty] | c.a | = | 0 | mm
=
| Radiography | [6 empty] | = | None
| P.W.H.T | [6 empty] | = | No
| Impact Tests | [6 empty] | = | No
| Maximum Allowable Stress (@ Design temp) |  |  |  | UG-23 & ASME II |  | Sd | = | 113.3333 | MPa
| Maximum Allowable Stress (@ Test Temp) |  |  |  | UG-23 & ASME II |  | Sa | = | 127.5 | MPa
| Longitudinal Joint Factor | [5 empty] | E | = | 0.7
| Inside length of major axis (Internal Diameter New) | [5 empty] | Di | = | 2190 | mm
| Inside length of the major axis (Internal Diameter Corroded) | [5 empty] | D | = | 2190 | mm
| Estimated Thinning Allowance | [6 empty] | = | 7 | %
| Plate Undertolerance | [6 empty] | = | 1 | mm
| Nominal Thickness | [6 empty] | = | 6 | mm
| Nominal Thickness Minus Thinning Allowance & Plate Undertolerance | [5 empty] | tmin | = | 4.58 | mm
| Minimum required thickness after forming = P D K / (2SE - 0.2P) | [5 empty] | t | = | 0.099931 | mm
[7 empty] | t + c | = | 0.099931 | mm
[6 empty] | (Since t min > t + c, The thickness used is SATISFACTORY) | Use | = | 6 | mm
4.0 | MINIMUM ROOF THICKNESS
4.1 | Minimum thickness as per |  |  |  | API 650 Clause 3.10.2 |  |  | = | 4.7 | mm |  | ANNULAR BOTTOM PLATE DESIGN:
| Corrosion allowance, c.a. | [6 empty] | = | 0 | mm |  | As per API 650 11th Ed. 2009 Add. 2 Sect. 5.5.2;
| Minimum thickness required | [6 empty] | = | 4.7 | mm |  | Minimum Annular plate Width shall be = |  |  | 215 tb |  | 28.62 | 727 | mm
| Therefore , use thickness of |  |  |  | 6 | mm is | satisfactory. | [7 empty] | ( GH )0.5
[16 empty] | or a Minimum of | 23.622 | 600 | mm
4.2 | SELF SUPPORTED CONE ROOF
| (1) Minimum thickness shall be the greater of the followings (a) and (b) :- | [10 empty] | Annular Plate width provided; in |  |  |  |  | 29.92 | 760 | mm
| (a) Minimum thickness as per |  |  |  | API 650 Clause 3.10.2 |  |  | = | 4.7625 | mm | [5 empty] | Where: tb = Annular plate thickness, mm
| (b) Minimum thickness, ( clause 3.10.6.1 ) | [14 empty] | H = maximum Design Liquid level, Meter
|  |  | Di | [12 empty] | G = liquid Specific gravity
|  | tmin | = |  |  |  |  | = | 1.7709 | mm
|  |  | 400 sin ß° | [8 empty] | HENCE, OK.
|  | ß° | = Roof slope |  |  |  |  | = | 15 | °
| Minimum thickness required (max. of (a) & (b)) | [6 empty] | = | 4.7625 | mm
4.2 | CHECK FOR ROOF LOADING
| Roof plate weight , @ assume Roof thk = |  |  |  |  | 6 | mm,wr | = | 0.00046205 | N/mm²
| Vacuum pressure , Va | [6 empty] | = | 0 | N/mm²
| Uniform live load , wl |  |  |  | @ | 25 | lbs/ft² | = | 0.0011962 | N/mm²
| Add. live load exceeding 122 kg/m², wa @ |  |  |  |  | 12 | lbs/ft² | = | 0.00057417 | N/mm²
| Total live load plus dead loads, wld | [6 empty] | = | 0.0022324 | N/mm²
[8 empty] | = | 46.6568 | lbs/ft²
[8 empty] | > | 45 | lbs/ft²
| The roof plate shall be increased by the following ratio , k | [6 empty] | = | 1.0182
| Minimum thickness required, tmin | [6 empty] | = | 4.8494 | mm
| Corrosion allowance, c.a. | [6 empty] | = | 0 | mm
| Therefore, minimum thickness ( + corrosion allowance ) | [6 empty] | = | 4.8494 | mm
| (2) Maximum thickness | [6 empty] | = | 6 | mm
| Therefore , use thickness of |  |  |  | 5.99 | mm is | satisfactory.
4.1 | INTERMEDIATE WIND GIRDER DESIGN
4.2 | ( Maximum Height Of The Unstiffened Shell )
|  |  |  | 100tt.corr ³ |  | 100 ²
|  | H1 | = 6(100tt.corr) |  | x | x k |  | = | 46668.1547 | mm
|  |  |  | D |  | V
where
|  | tt.corr | = Thickness of the top shell course (corroded) |  |  |  |  | = | 0.11811 | in | 3
|  | D | = Nominal tank diameter |  |  |  |  | = | 7.2178 | ft
|  | V | = Wind design speed ( @ |  |  | 44 | m/s ) | = | 98.4298 | miles/hr
|  | k | = Yield strength reduction factor ( Appendix M ) |  |  |  |  | = | 1
4.3 | Location Of Intermediate Wind Girder
| Course |  | Thickness. |  | Actual Width |  | Transposed Width
|  |  | t.corr |  | W |  | Wtr =W(tt.corr / t.corr)^2.5
|  |  | (mm) |  | (mm) |  | (mm)
| 1 (bottom) |  | 5 |  | 6914.2857 |  | 1928.0818
| 2 |  | 5 |  | 6914.2857 |  | 1928.0818
|  |  | 0 |  |  |  | #DIV/0!
|  |  | 0 |  |  |  | #DIV/0!
|  |  | #VALUE! |  |  |  | #VALUE!
|  |  | #VALUE! |  |  |  | #VALUE!
|  |  | 0 |  |  |  | #DIV/0!
|  |  | 0 |  |  |  | #DIV/0!
|  |  | #VALUE! |  |  |  | #VALUE!
|  |  |  | Height of transformed shell, H2 = |  |  | 3856.1635
REMARK : Let all 'Wtr' equal to zero for 'negative' t.corr
|  | Since H1 | > | H2 , therefore an intermediate wind girder is |  |  |  |  | not required. |  |  |  |  | VERIFICATION OF UNSTIFFENED SHELL FOR EXTERNAL PRESSURE
| No of Wind Girder required |  |  | = |  | H2 / H1 |  | = | 0
| THEREFORE , NO OF WIND GIRDER REQUIRED | [6 empty] | = | 0
Need not to be evaluated as the design external pressure is zero. As per Chapter 3, Clause 3.2.1.i, design external
5 | WIND DESIGN CALCULATION | [12 empty] | pressure shall not be less than 0.25 kPa. The tanks designed as per API 650 can sustain this minimum pressure.
| Design code | [6 empty] | : | ASCE -7
5.1 | GEOMETRIC DATA
| Internal design pressure, |  |  | Pi @ | 296.8506 | mbar |  | = | 0.029685 | N/mm²
| Diameter of tank, Di | [6 empty] | = | 2190 | mm
| Tank height , Hs | [6 empty] | = | 3026 | mm
| Roof slope, ß° | [6 empty] | = | 0 | °
| Roof height, Hr | [6 empty] | = | 428 | mm
| Height from tank bottom to shell centre, Ls | [6 empty] | = | 1513 | mm
| Height from tank bottom to roof centre,Lr | [6 empty] | = | 3454 | mm
| Min. depth of product ( always present in tank) , Hw | [6 empty] | = | 50 | mm
| Weight of tank,Wt |  | (@ | 1483.7835 | kg) |  |  | = | 14555.9164 | N
| Weight of product ( always present in tank) , Ww | [6 empty] | = | 1847.639 | N |  | 0.029685
5.2 | WIND FORCE CALCULATIONS
The wind loading shall be determined as follows : -
|  | H | = P.A.C.I | N
where
|  | P | = Wind dynamic pressure ( N/m² ) |  |  |  |  | = | 900
|  | Cr | = Shape factor for roof |  |  |  |  | = | 0.75
|  | Cs | = Shape factor for shell |  |  |  |  | = | 0.75
|  | Ar | = Projected area of roof ( = 0.5.Di.Hr ) |  |  |  |  | = | 0.46866 | m²
|  | As | = Projected area of shell ( = Di.Hs ) |  |  |  |  | = | 6.6269 | m²
|  | I | = Appurtenances |  |  |  |  | = | 1.18
| Total wind load exerted on roof, Fr | [6 empty] | = | 373.2877 | N
| Total wind load exerted on shell, Fs | [6 empty] | = | 5278.3577 | N
| Total wind moment on tank, Mwind ( = Fr.Lr + Fs.Ls ) | [6 empty] | = | 9275490.8965 | Nmm
6 | TANK STABILITY AGAINST WIND LOADING
6.1 | CASE 1 - EMPTY CONDITION
Resistance to overturning moment,
|  | Mres. | = 0.5Di.( Wt - 0.25 p Di².Pi ) |  |  |  |  | = | -106503200.0389 | Nmm
| Safety factor, Sa ( = Mres./Mwind ) | [6 empty] | = | 11.4822
[8 empty] | > | 1.5
|  | Since Sa | > | 1.5, therefore the tank is structurally
|  | stable. | Tank anchorage is |  | not required.
6.2 | CASE 2 - OPERATING CONDITION
Resistance to overturning moment,
|  | Mres. | = 0.5Di.( Wt + Ww - 0.25 p Di².Pi ) |  |  |  |  | = | -104480035.3246 | Nmm
| Safety factor, Sa ( = Mres./Mwind ) | [6 empty] | = | 11.2641
[8 empty] | > | 1.5
|  | Since Sa | > | 1.5, therefore the tank is structurally
|  | stable. | Tank anchorage is |  | not required.
7 | ANCHOR BOLT DESIGN
7.1 | GEOMETRIC DATA
| Number of bolts , N | [6 empty] | = | 35
| Diameter of anchor bolt, d | [6 empty] | = | 30 | mm
| Diameter of anchor bolt, d.corr ( less c.a.@ |  |  |  |  | 0 | mm) | = | 30 | mm
| Bolts circle diameter, Da | [6 empty] | = | 2320 | mm
| Root area of each hold down bolt, Ab | [6 empty] | = | 706.8583 | mm²
| Spacing between anchor bolts, Sb | [6 empty] | = | 208.2427 | mm
7.2 | BOLT MECHANICAL PROPERTIES
| Allowable stress, St.all | [6 empty] | = | 103 | N/mm²
7.3 | ANCHOR BOLTS DESIGN
Tensile force,
|  |  | 1 4.Mwind |  | Pi. pDi²
|  | T = |  | - Wt - |  |  |  | = | 3235.8692 | N
N Da 4
Tensile stress,
T
|  | sb | = |  |  |  |  | = | 4.5778 | N/mm²
Ab
|  | Since sb | < | St.all, therefore the anchor bolt size is |  |  |  | satisfactory.
8.0 | WEIGHT CALCULATION
8.1 | General
|  | Design code | [5 empty] | : | API 650
|  | Service | [5 empty] | : | Storage Tank
|  | Item number | [5 empty] | : | -
|  | Type of tank | [5 empty] | : | Self Supported
Cone Roof
|  | Inside diameter, Di | [5 empty] | = | 2200 | mm
|  | Tank height, H | [5 empty] | = | 3026 | mm
|  | Density of steel | [5 empty] | = | 8000 | kg/m³
8.2 | ERECTION WEIGHT
8.2.1 | Weight of bottom plate
|  | Material | [5 empty] | : | A 304
|  | Diameter of bottom plate | [5 empty] | = | 2300 | mm
|  | Bottom plate thickness | [5 empty] | = | 8 | mm
|  | Weight of bottom plate | [5 empty] | = | 265.9044 | kg
8.2.2 | Weight of shell
| Course | Material |  | Height | Length | Thickness | weight
| No. |  |  | (mm) | (mm) | (mm) | (kg)
| 1 (bottom) | A 304 |  | 1524 | 6914.2857 | 5 | 421.4949
| 2 | A 304 |  | 1524 | 6914.2857 | 5 | 421.4949
| 9 | A 304 |  | 0 | 6914.2857 | 4 | 0
| 10 | A 304 |  | 0 | 6914.2857 | 4 | 0
| 11 | A 304 |  | 0 | 6914.2857 | 4 | 0
[6 empty] | Total weight of shell |  | = | 842.9897 | kg
8.2.3 | Weight of head
|  | Material | [5 empty] | : | A 304
|  | Head plate thickness, tr | [5 empty] | = | 5.99 | mm
|  | Length of slope | [5 empty] | = | #REF! | mm
|  | Area of roof plate | [5 empty] | = | #REF! | mm²
|  | Weight of roof plate | [5 empty] | = | 264 | kg
8.2.3 | Weight of top curb angle
|  | Material | [5 empty] | : | 0
|  | Angle size | [5 empty] | : | #REF!
|  | Length of top curb angle | [5 empty] | = | 6911.5038 | mm
|  | Unit weight, wtca | [5 empty] | = | 5.91 | kg/m
|  | Weight of top curb angle | [5 empty] | = | 0 | kg
|  | Total Erection Weight, We @ ( |  |  | 10 | % additional weight ) |  | = | 1483.7835 | kg
8.3 | OPERATING WEIGHT
8.3.1 | Weight of liquid
|  | Specific gravity of liquid | [5 empty] | = | 1
|  | Maximum design liquid level | [5 empty] | = | 3026 | mm
|  | Volume of liquid in tank | [5 empty] | = | 11.5028 | m³
|  | Weight of liquid, Wliq. | [5 empty] | = | 11502.8158 | kg
|  | Total operating weight , Wo ( = We + Wliq. ) | [5 empty] | = | 12986.5994 | kg
8.4 | HYDROSTATIC TEST WEIGHT
8.4.1 | Weight of water
|  | Specific gravity of water | [5 empty] | = | 1
|  | Height of water | [5 empty] | = | 3026 | mm
|  | Volume of water in tank | [5 empty] | = | 11.5028 | m³
|  | Weight of water, Wh2o | [5 empty] | = | 11502.8158 | kg
|  | Total hydrostatics test weight , Wh ( = We + Wh2o ) | [5 empty] | = | 12986.5994 | kg
TABLE SHOWN BELOW ONLY FOR INFORMATION WHILE DOING THE LIFTING LUG CALCULATION!!
(HIDE THE TABLE WHEN PRINTING !!!)
1. | WEIGHT OF BOTTOM PLATE (+ % of increased weight) | [6 empty] | = | 3130.2266 | N
2. | WEIGHT OF SHELL (+ % of increased weight) | [6 empty] | = | 9923.6749 | N
3. | WEIGHT OF ROOF PLATE (+ % of increased weight) | [6 empty] | = | 3107.808 | N
[9 empty] | 16161.7095 | N
4. | TOTAL ERECTION WEIGHT |  |  |  | = | 1483.7835 | kg |  | 14555.9164 | N
Sd
St

## Shell & SE head
??? | [8 empty] | J1 used as a blank
Client | ??? |  |  | Date | ??/??/??
Description | ??? |  |  | Item No | ???
Prepared By | ??? |  |  | Calc No | ???
Yellow shaded cells are for user inputs
Pressure Vessel Design |  |  | (Heads 2:1 Semi-Ellipsoidal) | [5 empty] | THK= | 5
Design Code |  | ASME VIII Division 1 | [6 empty] | OD= | 2200
Internal Design Pressure |  |  |  |  | P | 0.00296 | Mpa | p | ID= | 2190
Liquid/ Packing Head | [5 empty] | 428 | mm | head
Specific Gravity Internals |  |  |  |  | g | 1 |  | sg
Liquid/ Packing Head Pressure |  |  |  |  | Ph | 0.00428 | Mpa | h
Design Pressure Including Head |  |  |  |  | P | 0.00724 | Mpa | ph
Design Temperature for Internal Pressure | [5 empty] | 40 | oC
Internal Corrosion Allowance |  |  |  |  | c.a | 0 | mm | ca
Radiography | [5 empty] | None
P.W.H.T | [5 empty] | No
Impact Tests | [5 empty] | No
Shell Data |  | Material | SS 304
Maximum Allowable Stress (@ Design temp) |  |  |  | UG-23 & ASME II | Sd | 113.3333 | MPa | fd
Maximum Allowable Stress (@ Test Temp) |  |  |  | UG-23 & ASME II | Sa | 127.5 | MPa | fa
Longitudinal Joint Factor |  |  |  | Table UW-12 | E | 0.7 |  | n (See Table)
Circumferential Weld Joint Efficiency |  |  |  | Table UW-12 | E | 0.7 |  | nc (See Table)
Fabricated from - | (Enter 1 for Plate, 2 for Pipe) |  | 1
Internal Diameter (new & uncorroded) | [5 empty] | 2190 | mm | idn
Plate Undertolerance | [5 empty] | 0.3 | mm | utol
Head Data |  | Material | SS 304
(Heads 2:1 Semi-Ellipsoidal)
Maximum Allowable Stress (@ Design temp) |  |  |  | UG-23 & ASME II | Sd | 113.3333 | MPa | fdh | 113.3333 | N/mm² | = | 16437.64 | psi
Maximum Allowable Stress (@ Test Temp) |  |  |  | UG-23 & ASME II | Sa | 127.5 | MPa | fah | 127.5 | N/mm² | = | 18492.345 | psi
Longitudinal Joint Factor |  |  |  |  | E | 0.7 |  | nh
Inside length of major axis (Internal Diameter New) |  |  |  | 0 | Di | 2190 | mm | idnh
Inside length of the major axis (Internal Diameter Corroded) |  |  |  |  | D | 2190 | mm | idch
Estimated Thinning Allowance | [5 empty] | 7 | % | ta
Plate Undertolerance | [5 empty] | 1 | mm | hutol
Comments:
Per ASME VIII Division 1 UG-16(e) - "The dimensional symbols used in design formulas throughout this division represent dimensions in the corroded condition".
2 : 1 Ellipsoidal Head Design |  |  |  | UG-32 (d)
With Static Head Pressure
Nominal Thickness | [5 empty] | 6 | mm | nth
Nominal Thickness Minus Thinning Allowance & Plate Undertolerance |  |  |  |  | tmin | 4.58 | mm | tminh
Minimum required thickness after forming = P D K / (2SE - 0.2P) |  |  |  |  | t | 0.099931 | mm | th
| (where K = 1) |  |  |  | t + c | 0.099931 | mm | tch
|  |  |  | (Since t min > t + c, The thickness used is SATISFACTORY) | Use | 6 | mm
Required Thickness For Nozzle Reinforcement (ie Seamless Sphere of Radius K1D)
tr = P K1 D / (2S - 0.2P) |  | (K1 = 0.9) |  |  | tr | 0.062956 | mm | trsphere
Maximum Allowable Design Pressure
P = 2 S E t / (DK + 0.2t) |  |  |  |  | Pmax | 0.33168 | MPag
With No Static Head Pressure
Nominal Thickness | [5 empty] | 6 | mm | ntho
Nominal Thickness Minus Thinning Allowance & Plate Undertolerance |  |  |  |  | tmin | 4.58 | mm | tminho
t = P D K / (2SE - 0.2P) |  |  |  |  | t | 0.040856 |  | tho
[5 empty] | t + c | 0.040856 | mm | tcho
|  |  |  | t min > t + c | Use | 6 | mm
Required Thickness For Nozzle Reinforcement (ie Seamless Sphere of Radius K1D)
tr = P K1 D / (2S - 0.2P) |  | (Where P = Design Pressure & K1 = 0.9) |  |  | t | 0.025739 | mm
Shell Design |  |  |  | UG-27
With Static Head Pressure
Nominal Thickness | [5 empty] | 25 | mm | nt
Minimum Thickness (Corroded & Plate Undertolerance) |  |  |  |  | t - c - utol | 24.7 | mm | tmin
Maximum Corroded Internal Radius |  |  |  |  | R | 1095 | mm | d
Minimum required thickness = P R / (SE - 0.6P) |  |  |  |  | t | 0.099936 | mm | t
Required Thickness |  |  |  |  | t + c | 0.099936 | mm
Available Thickness |  | 0 |  |  |  | 24.7 | mm | tc
|  | t avail > t + c |  | Use: |  | 25 | mm
Minimum Thickness For Nozzle Reinforcement (including static head)
t = P R / (S - 0.6P) |  |  |  |  | t | 0.069954 | mm | tnr
Maximum Allowable Design Pressure
P = S E t / (R + 0.6t) |  |  |  |  | Pmax | 1.7656 | MPag
With No Static Head Pressure
Nominal Thickness | [5 empty] | 25 | mm | nto
Minimum Thickness (Corroded & Plate Undertolerance) |  |  |  |  | tmin | 24.7 | mm | tmino
Maximum Corroded Internal Radius |  |  |  |  | R | 1095 | mm | d
t = P R / (SE - 0.6P) |  |  |  |  | t | 0.040856 | mm | do
Required Thickness |  |  |  |  | t + c | 0.040856 | mm | tco
Available Thickness |  | 0 |  |  |  | 24.7 | mm |  | (Nominal - Undertolerance)
|  | t avail > t + c |  | Use: |  | 25 | mm
Minimum Thickness For Nozzle Reinforcement (excluding static head)
t = P R / (S - 0.6P) |  |  |  |  | t | 0.028599 | mm | tnro
Hydrostatic Test Pressure @ Top of Vessel
1.5 P Sa / Sd | (Shell to Govern) |  |  |  |  | 0.004995 | MPag

## TANK DESIGN
DESIGN OF STEEL STORAGE TANKS AS PER API-650 (Diameter <=3m)
SELF-SUPPORTED CONE ROOF
DESIGN DATA
Service |  |  | HSD SERVICE |  | Allowable Design Stress (Sd) PSI |  |  | 23200 | See Table 3-2 on page
Capacity |  |  | 21.1879 |  | Allowable Test Stress (St) PSI |  |  | 24900 | 3-7 of API - 650
Type of tank |  |  | Self Supported Cone Roof |  | Specific Gravity of Liquid (G) |  |  | 0.87
Dia of tank (feet) |  |  | 10.004 |  | Corrosion Allowance (CA) (inches) |  |  | 0.11811 | By Client
Height of tank (feet) |  |  | 9.512
Slope of roof |  |  | 5
Slope of bottom |  |  | Flat Bottom | [6 empty] | Width | Length
[6 empty] | Full coarse Full width |  |  | A | 1219.5122 | 2440
Plate Data | [5 empty] | Full coarse Partial width |  |  | B | 1219.5122 | 2265
Plate width (meter) |  |  | 2.439 |  |  | Partial coarse Full width |  |  | C | 460.9756 | 2440
Plate height (meter) |  |  | 1.2195 |  |  | Partial coarse Partial width |  |  | D | 460.9756 | 2265
Den. of mat. (Kg/m3) |  |  | 7850
INPUT
OUTPUT
SHELL
By one foot method. See sec. 3.6.3.2
on page 3-7 of API - 650
Course # | Liq. height |  | Height of | Design shell | Design shell | Hyd. shell | Adopted shell | Recommended
from bottom | in tank |  | each Course | thickness | thickness | thickness | thickness | by Client
of tank | (H) |  |  | (td) | (td) | (tt) |  | Thickness
| ft |  | mm | inches | mm | inches | (mm) | (mm)
1 | 9.512 |  | 1219.5122 | 0.12641 | 3.2109 | 0.0088916 | 5 | 5 | [8 empty] | 3.9286
2 | 5.512 |  | 1219.5122 | 0.12251 | 3.1118 | 0.0047132 | 5 | 5 | [8 empty] | 3.9286
3 | 1.512 |  | 460.9756 | 0.11861 | 3.0127 | 0.00053483 | 5 | 5 | [8 empty] | 3.9286
3.9286
3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
|  |  | 0 |  | 0 | [11 empty] | 3.9286
3.9286
Note: | According to sec. 3.6.1.1 min. thk.of tank of dia. <50ft should be 3/16 inches (4.76mm). | [15 empty] | 3.9286
Course # | # of full |  | Size of full plate |  | # of partial | Sise of Shell |  | Weight
from bottom | plates in |  | in each course |  | plates in | partial plate |  | of each
of tank | shell per |  | (Width) | (Height) | shell per | (Width) | (Height) | course
| course |  | mm | mm | course | mm | mm | Kg
1 | 3 |  | 2440 | 1219.5122 | 1 | 2265 | 1219.5122 | 458.7942
2 | 3 |  | 2440 | 1219.5122 | 1 | 2265 | 1219.5122 | 458.7942
3 | 3 |  | 2440 | 460.9756 | 1 | 2265 | 460.9756 | 173.4242
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[6 empty] | Total wt. of shell plate Kg. |  | 1091.0126
BOTTOM PLATE
Accordig to sec. 3.4.1 on page 3-5 of API 650, minimum thickness of the bottom plate should be 1/4 inches (6.35 mm)
without corrossion allowance,
Corrosion Allowance (mm) |  |  | 3
Thickness of Bottom Plate |  |  | 10
Weight of Bottom Plate |  |  | 689
CURB ANGLE
See Section 3.1.5.9 ( e ) of API 650 page 3-4
Size of curb angle |  |  | 2x2x3/16
Weight of Curb Angle |  |  | 36
INTERMEDIATE WIND GIRDER (Using top course thickness)
See section 3.9.7.1 on page 3-39 of API 650
| By Client | [10 empty] | CURB ANGLE | Weight
Top shell | Wind |  | Vertical | Vertical | Min. req. | Remarks | [5 empty] | 2x2x3/16 | 3.75
course | velocity |  | dist. b/w | dist. b/w | section | [6 empty] | 2x2x1/4 | 5.13
thickness |  |  | wind girder | wind girder | modulus | [6 empty] | 3x3x3/8 | 11.8
|  |  | & curb angle | & curb angle
(t) | (V) |  | (H1) | with 12%safety | (Z)
inches | miles/hours |  | feet | feet | inch3
0.19685 | 110 |  | 269.4301 | 237.0985 |  | not req.
0
'file:///tmp/in/input.xls'#$TANK DESIGN
DESIGN OF TANK ROOF. ( SELF-SUPPORTED CONE ROOF )
As per API 650 1993 Section 3.10.5 on page 3-45,
Min plate thickness should be not less than 3/16" (4.76 mm)
without corrosion allowance.
Corrosion Allowance |  |  | 3 | Angle (Degree) | 44.9942
Thickness of Roof Plate |  |  | 7.7625 | Min. thk Calculated (in) | 0.035373
Slope of Roof |  |  | 1 | Min. thk Calculated (mm) | 0.89848 | [5 empty] | m | h
|  |  |  | Min. Recommended | 4.7625 | See sec. 3.10.5.1 on page 3-45
INPUT |  |  |  | thk (mm) |  | API 650
OUTPUT | [10 empty] | r | r
Radius of | Thickness of |  | Height of | Slant ht. | Surface area | Surface area | Weight of | Weight of | Unit load | Live load | Over lape | Total roof
Tank | Roof plate |  | roof cone | of roof | of roof | of roof | roof plate | roof plate | of roof |  | of roof | load
( r ) ft | ( t ) ft |  | (h) ft | (m) ft | feet2 | meter2 | Kg. | lbs. | lb/ft2 | lb/ft2 | 10% | lb/ft2
5.002 | 0.025468 |  | 5.002 | 7.0739 | 111.1609 | 10.3325 | 629.7773 | 1388.659 | 12.4923 | 25 | 1.2492 | 38.7416
'file:///tmp/in/input.xls'#$TANK DESIGN
DESIGN OF STEEL STORAGE TANKS AS PER API-650 (Diameter greater than 3m but less than 10m)
Supported Cone Roof Without Column
DESIGN DATA
Service |  |  | HFO |  | Allowable Design Stress (Sd) PSI |  |  | 16437.64 | See Table 3-2 on page
Capacity |  |  | 248.9467 |  | Allowable Test Stress (St) PSI |  |  | 127.5 | 3-7 of API - 650
Type of tank |  |  | Supported cone roof |  | Specific Gravity of Liquid (G) |  |  | 0.96
Dia of tank (feet) |  |  | 17.22 |  | Corrosion Allowance (CA) |  |  | 0
Height of tank (feet) |  |  | 37.72
Slope of roof |  |  | 1:36
Slope of bottom |  |  | 1:100. | [6 empty] | Width | Length
[6 empty] | Full coarse Full width |  |  | A | 464.6341 | 2439.0244
Plate Data | [5 empty] | Full coarse Partial width |  |  | B | 464.6341 | 1859.2151
Plate width (meter) |  |  | 2.439 |  |  | Partial coarse Full width |  |  | C | 348.7805 | 2439.0244
Plate height (meter) |  |  | 0.46463 |  |  | Partial coarse Partial width |  |  | D | 348.7805 | 1859.2151
Den. of mat. (Kg/m3) |  |  | 8100
1080
INPUT | [8 empty] | 540
OUTPUT | [8 empty] | 810
SHELL
By one foot method. See sec. 3.6.3.2
on page 3-7 of API - 650
Course # | Liq. height |  | Height of | Design shell | Design shell | Hyd. shell | Adopted shell | Selected Min.
from bottom | in tank |  | each Course | thickness | thickness | thickness | thickness | shell thickness
of tank | (H) |  |  | (td) | (td) | (tt)
| ft |  | mm | inches | mm | inches | (mm) | (mm)
1 | 37.72 |  | 464.6341 | 0.096015 | 2.4388 | 12.8943 | 7 | 10
2 | 36.196 |  | 464.6341 | 0.09203 | 2.3376 | 12.3592 | 7 | 10
3 | 34.672 |  | 464.6341 | 0.088046 | 2.2364 | 11.824 | 7 | 9
4 | 33.148 |  | 464.6341 | 0.084061 | 2.1351 | 11.2889 | 7 | 9
5 | 31.624 |  | 464.6341 | 0.080076 | 2.0339 | 10.7537 | 7 | 8
6 | 30.1 |  | 464.6341 | 0.076091 | 1.9327 | 10.2186 | 7 | 8
7 | 28.576 |  | 8712.1951 | 0.072106 | 1.8315 | 9.6834 | 7 | 7
0
0
0
Note: | According to sec. 3.6.1.1 min. thk.of tank of dia. 50ft to <120ft should be 1/4 inches.
Course # | # of full |  | Size full plate |  | # of partial | Sise of Shell |  | Weight
from bottom | plates in |  | in each course |  | plates in | partial plate |  | of each
of tank | shell per |  | (Width) | (Height) | shell per | (Width) | (Height) | course
| course |  | mm | mm | course | mm | mm | Kg
1 | 6 |  | 2440.0244 | 464.6341 | 1 | 1860 | 464.6341 | 620.989
2 | 6 |  | 2440.0244 | 464.6341 | 1 | 1860 | 464.6341 | 620.989
3 | 6 |  | 2440.0244 | 464.6341 | 1 | 1860 | 464.6341 | 558.8901
4 | 6 |  | 2440.0244 | 464.6341 | 1 | 1860 | 464.6341 | 558.8901
5 | 6 |  | 2440.0244 | 464.6341 | 1 | 1860 | 464.6341 | 496.7912
6 | 6 |  | 2440.0244 | 464.6341 | 1 | 1860 | 464.6341 | 496.7912
7 | 6 |  | 2440.0244 | 8712.1951 | 1 | 1860 | 8712.1951 | 8150.7664
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[7 empty] | 0 | 0
[6 empty] | Total wt. of shell plate Kg. |  | 11504.1073
BOTTOM PLATE
Accordig to sec. 3.4.1 on page 3-5 of API 650, minimum thickness of the bottom plate should be 1/4 inches without corrossion allowance,
so when we add 3mm of corrossion allowance then the bottom plate thickness comes out to be 10 mm.
Thickness of Bottom Plate |  |  | 10
Weight of Bottom Plate |  |  | 2104.1406
CURB ANGLE
See Section 3.1.5.9 ( e ) of API 650 page 3-4
Size of curb angle |  |  | 2x2x3/16
Weight of Curb Angle |  |  | 19
INTERMEDIATE WIND GIRDER (Using top course thickness)
See section 3.9.7.1 on page 3-9 of API 650
By Client
Top shell | Wind |  | Vertical | Vertical | Min. req. | Remarks
course | velocity |  | dist. b/w | dist. b/w | section
thickness |  |  | wind girder | wind girder | modulus
|  |  | & curb angle | & curb angle
(t) | (V) |  | (H1) | with 12%safety | (Z)
inches | miles/hours |  | feet | feet | inch3
0.27559 | 110 |  | 276.6795 | 243.478 | 8.2043 | not req.
0 | 110 |  | 276.6795 | 243.478 | 8.2043 | not req.
'file:///tmp/in/input.xls'#$TANK DESIGN
DESIGN OF TANK ROOF. ( SUPPORTED CONE ROOF )
As per API 650 1993 Section 3.10.2 on page 3-41, Min plate thickness should be not less than 3/16" (4.76 mm).
Use 8 mm thick plate with corrosion allowance (3mm) .
Slope of Roof = 1 : |  |  | 36 | [7 empty] | m | h
INPUT
OUTPUT | [10 empty] | r | r
Radius of | Thickness of |  | Height of | Radius of | Surface area | Surface area | Weight of | Weight of | Unit load | Live load | Over lape | Total roof
Tank | Roof plate |  | roof cone | cone | of cone roof | of cone roof | roof plate | roof plate | of roof |  | of roof | load
( r ) ft | ( t ) ft |  | (h) ft | ( r ) ft | feet2 | meter2 | Kg. | lbs. | lb/ft2 | lb/ft2 | 10% | lb/ft2
8.61 | 0.016404 |  | 0.23917 | 8.6133 | 233.0726 | 21.6642 | 851 | 1877 | 8.0533 | 25 | 0.80533 | 33.8586
'file:///tmp/in/input.xls'#$TANK DESIGN
RAFTER DESIGN
NUMBER OF RAFTERS
See sec. 3.10.4.5 on page 3-45 of API - 650
INPUT
OUTPUT
Note : For the Tanks upto 10 m Dia there should be one ring of Rafters.
For the Tanks Dia greater than 10m but less than 20 m there should be two rings of Rafters.
Inner Ring's Dia is 2/3 of the Outer Ring Dia.
For the Tanks Dia greater than 20m but less than 35 m there should be three rings of Rafters.
Intermediate Ring's Dia is 2/3 of the Outer Ring's Dia & Inner Ring's Dia is 1/2 of the Intermediate Ring's Dia.
Circumferencial | Min Spacing |  | Min No | Actual No
Length | of Rafters |  | of Rafters | of Rafters
(L) ft | (s) ft |  | # | #
54.0982 | 6.2832 |  | 8.61 | 9
DESIGN OF RAFTERS
Rafters are fixed at one end (Shell)and free but guided at the other end.
Uniform load over entire span.
INPUT | [5 empty] | 0
OUTPUT
Length of | Area |  | No. of Rafter | Weight on each | Distri-Load | Allowable stress | Allowable stress | Bending Moment | Section | Section
Rafters |  |  | selected | Rafter | on Rafter | for bending | for bending |  | Modulus | Modulus
ft | m2 |  | # | lbs | lbs/in | PSI | N/m2 | lbs-in | in3 | cm3
8.61 | 2.4071 |  | 9 | 876.8349 | 8.4866 | 18000 | 124020000 | 15099.0969 | 0.83884 | 13.7486
Use Menu Control A - Rafter - Selection of Section
SELECTED SECTION |  |  | I-160
Weight / Length |  |  | 17.9 |  | Total weight of
Load |  |  | 175.599 |  | Rafter (outer)(Kg) | 423
Section Modulus |  |  | 116.9311
Second Moment of Area
Bending Moment |  |  | 151.2484
Section Modulus |  |  | 1.2195
Due to the Section
Total Section Modulus |  |  | 1.2195
Remarks |  |  | Safe
Actual Stress in Rafter |  |  | 2116.4102
Remarks |  |  | Safe
Max. Allowable deflection |  |  | 7.2917
Max. Deflection at free end |  |  | #DIV/0!
Remarks |  |  | #DIV/0!
DESIGN OF STEEL STORAGE TANKS AS PER API-650 (Diameter greater than 3m but less than 10m)
Supported Cone Roof With Column
DESIGN DATA
Service |  |  | HFO |  | Allowable Design Stress (Sd) PSI |  |  | 16437.64 | See Table 3-2 on page
Capacity |  |  | 249.1372 |  | Allowable Test Stress (St) PSI |  |  | 18492.345 | 3-7 of API - 650
Type of tank |  |  | Supported cone roof |  | Specific Gravity of Liquid (G) |  |  | 1
Dia of tank (feet) |  |  | 17.2244 |  | Corrosion Allowance (CA) |  |  | 0 | By Client
Height of tank (feet) |  |  | 37.7295
Slope of roof |  |  | 1:5
Slope of bottom |  |  | 1:100. | [6 empty] | Width | Length
[6 empty] | Full coarse Full width |  |  | A | 1524 | 16500
Plate Data | [5 empty] | Full coarse Partial width |  |  | B | 1524 | 1859.2151
Plate width (meter) |  |  | 16.5 |  |  | Partial coarse Full width |  |  | C | 348.7805 | 16500
Plate height (meter) |  |  | 1.524 |  |  | Partial coarse Partial width |  |  | D | 348.7805 | 1859.2151
Den. of mat. (Kg/m3) |  |  | 8100
1080
INPUT | [8 empty] | 540
OUTPUT | [8 empty] | 810
SHELL
By one foot method. See sec. 3.6.3.2
on page 3-7 of API - 650
Course # | Liq. height | Liq. height | Height of | Design shell | Design shell | Hyd. shell | Hyd. shell | Selected Min.
from bottom | in tank | in tank | each Course | thickness | thickness | thickness | thickness | shell thickness
of tank | (H) | (H) |  | (td) | (td) | (tt)
| ft | mm | mm | inches | mm | inches | (mm) | (mm)
1 | 37.7295 | 11499.9653 | 1524 | 0.2192 | 5.5676 | 0.088949 | 2.2593 | 5 | OK
2 | 32.7308 | 9976.355 | 1524 | 0.18936 | 4.8098 | 0.076843 | 1.9518 | 5 | OK
3 | 27.7321 | 8452.745 | 1524 | 0.15953 | 4.0521 | 0.064738 | 1.6443 | 5 | OK
4 | 22.7334 | 6929.135 | 1524 | 0.1297 | 3.2944 | 0.052632 | 1.3369 | 4 | OK
5 | 17.7347 | 5405.525 | 1524 | 0.099869 | 2.5367 | 0.040527 | 1.0294 | 4 | OK
6 | 12.7359 | 3881.916 | 1524 | 0.070038 | 1.779 | 0.028421 | 0.7219 | 4 | OK
7 | 7.7372 | 2358.306 | 1524 | 0.040207 | 1.0212 | 0.016316 | 0.41442 | 3 | OK
8 | 2.7385 | 834.696 | 1524 | 0.010375 | 0.26353 | 0.0042102 | 0.10694 | 3 | OK
0
0
0
0
Note: | According to sec. 3.6.1.1 min. thk.of tank of dia. 50ft to <120ft should be 1/4 inches.
Course # | # of full |  | Size full plate |  | # of partial | Sise of Shell |  | Weight
from bottom | plates in |  | in each course |  | plates in | partial plate |  | of each
of tank | shell per |  | (Width) | (Height) | shell per | (Width) | (Height) | course
| course |  | mm | mm | course | mm | mm | Kg
1 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 1018.413 |  |  |  |  | 0.99985
2 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 1018.413 |  |  |  | ``` | 0.99985
3 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 1018.413 |  |  |  |  | 0.99985
4 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 814.7304 |  |  |  |  | 0.99985
5 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 814.7304 |  |  |  |  | 0.99985
6 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 814.7304 |  |  |  |  | 0.99985
7 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 611.0478 |  |  |  |  | 0.99985
8 | 1 |  | 16500 | 1524 | 0 | -2 | 1524 | 611.0478 |  |  |  |  | 0.99985
[7 empty] | 0 | 0 |  |  |  |  | 0.99985
[7 empty] | 0 | 0 |  |  |  |  | 0.99985
[7 empty] | 0 | 0 |  |  |  |  | 0.99985
[7 empty] | 0 | 0 |  |  |  |  | 0.99985
[7 empty] | 0 | 0 |  |  |  |  | 0.99985
[6 empty] | Total wt. of shell plate Kg. |  | 6721.5258
BOTTOM PLATE
Accordig to sec. 3.4.1 on page 3-5 of API 650, minimum thickness of the bottom plate should be 1/4 inches without corrossion allowance,
so when we add 3mm of corrossion allowance then the bottom plate thickness comes out to be 10 mm.
Thickness of Bottom Plate |  |  | 6
Weight of Bottom Plate |  |  | 1263.131
CURB ANGLE
See Section 3.1.5.9 ( e ) of API 650 page 3-4
Size of curb angle |  |  | 2x2x3/16
Weight of Curb Angle |  |  | 19
INTERMEDIATE WIND GIRDER (Using top course thickness)
See section 3.9.7.1 on page 3-9 of API 650
By Client
Top shell | Wind |  | Vertical | Vertical | Min. req. | Remarks
course | velocity |  | dist. b/w | dist. b/w | section
thickness |  |  | wind girder | wind girder | modulus
|  |  | & curb angle | & curb angle
(t) | (V) |  | (H1) | with 12%safety | (Z)
inches | miles/hours |  | feet | feet | inch3
0.11811 | 80 |  | 62.8744 | 55.3294 | 1.8654 | not req.
0.15748 | 110 |  | 131.142 | 115.405 | 3.8887 | not req.
'file:///tmp/in/input.xls'#$TANK DESIGN
DESIGN OF TANK ROOF. ( SUPPORTED CONE ROOF )
As per API 650 1993 Section 3.10.2 on page 3-41, Min plate thickness should be not less than 3/16" (4.76 mm).
Use | 5 | mm thick plate | mm Roof plate
Slope of Roof = | 15 |  | ° | [7 empty] | m | h
INPUT
OUTPUT | [10 empty] | r | r
Radius of | Thickness of |  | Height of | Slant ht. | Surface area | Surface area | Weight of | Weight of | Unit load | Live load | Over lape | Total roof
Tank | Roof plate |  | roof cone | of roof | of roof | of roof | roof plate | roof plate | of roof |  | of roof | load
( r ) ft | ( t ) ft |  | (h) ft | (m) ft | feet2 | meter2 | Kg. | lbs. | lb/ft2 | lb/ft2 | 10% | lb/ft2
8.6122 | 0.022966 |  | 0.57415 | 8.6313 | 233.5294 | 21.7067 | 1193.0887 | 2630.7605 | 11.2652 | 25 | 1.1265 | 37.3917
NUMBER OF RAFTERS
See sec. 3.10.4.5 on page 3-45 of API - 650
INPUT
OUTPUT
Circumferencial | Min Spacing |  | Min No | Actual No
Length | of Rafters |  | of Rafters | of Rafters
(L) ft | (s) ft |  | # | #
54.1121 | 6.2832 |  | 8.6122 | 9
DESIGN OF RAFTERS
INPUT | [5 empty] | 0
OUTPUT
Length of | Area |  | No. of Rafter | Weight on each | Distri-Load | Allowable stress | Allowable stress | Bending Moment | Section | Section
Rafters |  |  | selected | Rafter | on Rafter | for bending | for bending |  | Modulus | Modulus
ft | m2 |  | # | lbs | lbs-in | PSI | N/m2 | lbs-in | in3 | cm3
8.6122 | 2.4119 |  | 9 | 970.2301 | 9.3881 | 18000 | 124020000 | 12533.7306 | 0.69632 | 11.4127
SELECTED SECTION |  |  | W 6 x 20
AISC STANDARD
Weight / Length |  |  | 29.7506 |  | Total weight of
Load |  |  | 291.8531 |  | Rafter (Kg) | 704
Section Modulus |  |  | 219.626
Bending Moment |  |  | 251.51
Section Modulus |  |  | 2.028
Due to the Section
Total Section Modulus |  |  | 13.4406
Remarks |  |  | Safe
'file:///tmp/in/input.xls'#$TANK DESIGN
CENTER COLUMN DESIGN
INPUTS
OUTPUTS
Load on | Total wt. on |  | Selected | Size of | Length of | Unit wt. | Misc. | Wt. of | Total | Outside | Inside | Radius of | Slenderness
rafter | Center column |  | Member | Member | Column |  | wt. | Column | Weight | Diameter | Diameter | Gyration | Ratio
lbs. | lbs. |  |  | DN | (L) feet | lbs/ft | lbs. | Lbs | lbs. | (R)inches | inches | (r) inches | L/r
3
8732.0711 | 4366.0355 |  | 40 | 150 | 38.3037 | 117.4307 | 1102.5 | 4498.0297 | 9966.5652 | 6.6252 | 0 | 1.6563 | 277.5128
CHECKING OF COLUMN IN COMPRESSION
See section 3.10.3.3 on page 3-44 of API - 650
If L/r < 120 then Cma= [1-(L/r)^2/34700](33000/Fs)*Y
If 120 < L/r < 131.7 then Cma= {[1-(L/r)^2/34700](33000/Fs)*Y}/[1.6*(L/200*r)]
When L/r > 131.7 then Cma= {149000000*Y}/{(L/r)^2[1.6-(L/r*200)]
Where
Cma= Max. allowable compression, in PSI
L = Unbraced length of column, in inches
r = Least radius of gyration of column, in inches
Y = 1 for structural or tubular section that have t/r value greater than or equal to 0.015
For tubular section that have t/r values < 0.015
Y = {(200/3)(t/R)}{2-(200/3)(t/R)}
t/r | Cma |  | Cinduced | Remarks | Buckling
| PSI |  | PSI
2 | 9107.3583 |  | 126.6484 | Safe | Not Safe
'file:///tmp/in/input.xls'#$TANK DESIGN
DESIGN OF STEEL STORAGE TANKS AS PER API-650 (Diametet greater than 10 m but less than 20m)
Supported Cone Roof With Column
DESIGN DATA
Service |  |  | HFO |  | Allowable Design Stress (Sd) PSI |  |  | 23200 | See Table 3-2 on page
Capacity |  |  | 2739.0761 |  | Allowable Test Stress (St) PSI |  |  | 24900 | 3-7 of API - 650
Type of tank |  |  | Supported cone roof |  | Specific Gravity of Liquid (G) |  |  | 0.96
Dia of tank (feet) |  |  | 49.2 |  | Corrosion Allowance (CA) |  |  | 0.11811 | By Client
Height of tank (feet) |  |  | 50.84
Slope of roof |  |  | 1:5
Slope of bottom |  |  | 1:100. | [6 empty] | Width | Length
[6 empty] | Full coarse Full width |  |  | A | 1219.5122 | 2439.0244
Plate Data | [5 empty] | Full coarse Partial width |  |  | B | 1219.5122 | 1859.2151
Plate width (meter) |  |  | 2.439 |  |  | Partial coarse Full width |  |  | C | 348.7805 | 2439.0244
Plate height (meter) |  |  | 1.2195 |  |  | Partial coarse Partial width |  |  | D | 348.7805 | 1859.2151
Den. of mat. (Kg/m3) |  |  | 7850
1080
INPUT | [8 empty] | 540
OUTPUT | [8 empty] | 810
SHELL
By one foot method. See sec. 3.6.3.2
on page 3-7 of API - 650
Course # | Liq. height |  | Height of | Design shell | Design shell | Hyd. shell | Adopted shell | Selected Min.
from bottom | in tank |  | each Course | thickness | thickness | thickness | thickness | shell thickness
of tank | (H) |  |  | (td) | (td) | (tt)
| ft |  | mm | inches | mm | inches | (mm) | (mm)
1 | 50.84 |  | 1219.5122 | 0.38193 | 10 | 0.25605 | 10 | 10
2 | 46.84 |  | 1219.5122 | 0.36075 | 10 | 0.2355 | 10 | 10
3 | 42.84 |  | 1219.5122 | 0.33958 | 9 | 0.21495 | 9 | 9
4 | 38.84 |  | 1219.5122 | 0.31841 | 9 | 0.1944 | 9 | 9
5 | 34.84 |  | 1219.5122 | 0.29723 | 8 | 0.17385 | 8 | 8
6 | 30.84 |  | 1219.5122 | 0.27606 | 8 | 0.1533 | 8 | 8
7 | 26.84 |  | 1219.5122 | 0.25489 | 7 | 0.13275 | 7 | 7
8 | 22.84 |  | 1219.5122 | 0.23371 | 6 | 0.1122 | 7 | 7
9 | 18.84 |  | 1219.5122 | 0.21254 | 6 | 0.09165 | 7 | 7
10 | 14.84 |  | 1219.5122 | 0.19137 | 5 | 0.071101 | 7 | 7
11 | 10.84 |  | 1219.5122 | 0.1702 | 5 | 0.050552 | 7 | 7
12 | 6.84 |  | 1219.5122 | 0.14902 | 4 | 0.030002 | 7 | 7
13 | 2.84 |  | 865.8537 | 0.12785 | 4 | 0.0094527 | 7 | 7
Note: | According to sec. 3.6.1.1 min. thk.of tank of dia. 50ft to <120ft should be 1/4 inches.
Course # | # of full |  | Size full plate |  | # of partial | Sise of Shell |  | Weight
from bottom | plates in |  | in each course |  | plates in | partial plate |  | of each
of tank | shell per |  | (Width) | (Height) | shell per | (Width) | (Height) | course
| course |  | mm | mm | course | mm | mm | Kg
1 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4513.1242 |  |  |  |  | 19.3208
2 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4513.1242 |  |  |  | ``` | 19.3208
3 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4061.8118 |  |  |  |  | 19.3208
4 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4061.8118 |  |  |  |  | 19.3208
5 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3610.4994 |  |  |  |  | 19.3208
6 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3610.4994 |  |  |  |  | 19.3208
7 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3159.187 |  |  |  |  | 19.3208
8 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3159.187 |  |  |  |  | 19.3208
9 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3159.187 |  |  |  |  | 19.3208
10 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3159.187 |  |  |  |  | 19.3208
11 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3159.187 |  |  |  |  | 19.3208
12 | 19 |  | 2440.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3159.187 |  |  |  |  | 19.3208
|  |  |  | 0 |  |  | 0 | 0 |  |  |  |  | 19.3208
|  |  |  | 0 |  |  | 0 | 0 |  |  |  |  | 19.3208
|  |  |  | 0 |  |  | 0 | 0 |  |  |  |  | 19.3208
|  |  |  | 0 |  |  | 0 | 0 |  |  |  |  | 19.3208
|  |  |  | 0 |  |  | 0 | 0 |  |  |  |  | 19.3208
[6 empty] | Total wt. of shell plate Kg. |  | 43325.9927
BOTTOM PLATE
Accordig to sec. 3.4.1 on page 3-5 of API 650, minimum thickness of the bottom plate should be 1/4 inches without corrossion allowance,
so when we add 3mm of corrossion allowance then the bottom plate thickness comes out to be 10 mm.
Thickness of Bottom Plate |  |  | 10
Weight of Bottom Plate |  |  | 16646.5141
CURB ANGLE
See Section 3.1.5.9 ( e ) of API 650 page 3-4
Size of curb angle |  |  | 2x2x3/16
Weight of Curb Angle |  |  | 69
INTERMEDIATE WIND GIRDER (Using top course thickness)
See section 3.9.7.1 on page 3-9 of API 650
By Client
Top shell | Wind |  | Vertical | Vertical | Min. req. | Remarks
course | velocity |  | dist. b/w | dist. b/w | section
thickness |  |  | wind girder | wind girder | modulus
|  |  | & curb angle | & curb angle
(t) | (V) |  | (H1) | with 12%safety | (Z)
inches | miles/hours |  | feet | feet | inch3
0.27559 | 110 |  | 57.29 | 50.4152 | 13.8679 | Wind girder req.
0.27559 | 110 |  | 57.29 | 50.4152 | 13.8679 | Wind girder req.
'file:///tmp/in/input.xls'#$TANK DESIGN
DESIGN OF TANK ROOF. ( SUPPORTED CONE ROOF )
As per API 650 1993 Section 3.10.2 on page 3-41, Min plate thickness should be not less than 3/16" (4.76 mm).
Use 8 mm thick plate with corrosion allowance (3mm) .
Slope of Roof = 1 : |  |  | 5 | [7 empty] | m | h
INPUT
OUTPUT | [10 empty] | r | r
Radius of | Thickness of |  | Height of | Radius of | Surface area | Surface area | Weight of | Weight of | Unit load | Live load | Over lape | Total roof
Tank | Roof plate |  | roof cone | cone | of cone roof | of cone roof | roof plate | roof plate | of roof |  | of roof | load
( r ) ft | ( t ) ft |  | (h) ft | ( r ) ft | feet2 | meter2 | Kg. | lbs. | lb/ft2 | lb/ft2 | 10% | lb/ft2
24.6 | 0.026247 |  | 4.92 | 25.0872 | 1977.2129 | 183.7832 | 11544.5385 | 25455.7074 | 12.8745 | 25 | 1.2875 | 39.162
'file:///tmp/in/input.xls'#$TANK DESIGN
NUMBER OF RAFTERS
See sec. 3.10.4.5 on page 3-45 of API - 650
INPUT
OUTPUT
Note : For the Tanks upto 10 m Dia there should be one ring of Rafters.
For the Tanks Dia greater than 10m but less than 20 m there should be two rings of Rafters.
Inner Ring's Dia is 2/3 of the Outer Ring Dia.
For the Tanks Dia greater than 20m but less than 35 m there should be three rings of Rafters.
Intermediate Ring's Dia is 2/3 of the Outer Ring's Dia & Inner Ring's Dia is 1/2 of the Intermediate Ring's Dia.
Outer Ring
Circumference | Min Spacing |  | Min No | Actual No
of Tank | of Rafters |  | of Rafters | of Rafters
(L) ft | (s) ft |  | # | #
154.5664 | 6.2832 |  | 24.6 | 28
As per sketch 'A'
Inner Ring
Circumferencial | Min Spacing |  | Min No | Actual No
Length | of Rafters |  | of Rafters | of Rafters
(L) ft | (s) ft |  | # | #
103.0442 | 5.5 |  | 18.7353 | 16
As per sketch 'A'
0
DESIGN OF RAFTERS
INPUT | [5 empty] | 0
OUTPUT
Rafters of Outer Ring (R - 2).
Length of | Area |  | No. of Rafter | Weight on each | Distri-Load | Allowable stress | Allowable stress | Bending Moment | Section | Section
Rafters |  |  | selected | Rafter | on Rafter | for bending | for bending |  | Modulus | Modulus
ft | m2 |  | # | lbs | lbs-in | Psi | N/m2 | lbs-in | in3 | cm3
14.268 | 6.4978 |  | 28 | 2737.673 | 15.9896 | 18000 | 124020000 | 58591.6775 | 3.2551 | 53.351
Rafter of Outer Ring (R-2) |  |  | C 7 x 14.775
Weight / Length |  |  | 21.941 |  | Total weight of
Load |  |  | 215.2416 |  | Rafter (outer)(Kg) | 2673
Section Modulus |  |  | 127.5142
Bending Moment |  |  | 509.1137
Section Modulus |  |  | 4.1051
Due to the Section
Total Section Modulus |  |  | 57.4561
Remarks |  |  | Safe
Rafters of Inner Ring (R - 1).
Length of | Area |  | No. of Rafter | Weight on each | Distri-Load | Allowable stress | Allowable stress | Bending Moment | Section | Section
Rafters |  |  | selected | Rafter | on Rafter | for bending | for bending |  | Modulus | Modulus
ft | m2 |  | # | lbs | lbs-in | Psi | N/m2 | lbs-in | in3 | cm3
15.17 | 4.6948 |  | 16 | 1978.0079 | 10.8658 | 18000 | 124020000 | 45009.5691 | 2.5005 | 40.9837
SELECTED SECTION |  |  | W 10 x 17
AISC STANDARD
Weight / Length |  |  | 25.288 |  | Total weight of
Load |  |  | 248.0751 |  | Rafter (outer)(Kg) | 1872
Section Modulus |  |  | 265.518
Bending Moment |  |  | 663.3102
Section Modulus |  |  | 5.3484
Due to the Section
Total Section Modulus |  |  | 46.3321
Remarks |  |  | Safe
'file:///tmp/in/input.xls'#$TANK DESIGN
U 50 x 300
INPUT
OUTPUT
From Sketch - A it can be seen that Girder G-2 bears Half of the Load of Rafter R-2 & Half of the Rafter R-1.
So the Load On Girder G-2 is [( Load of Rafters R-1 x No of Rafters R-1 )/2] + [(Load of Rafters R-2 x No of Rafters R-2)/2].
For Safety we consider that R-1 = R-2 & Load of R-1 = Load of R-2.
No of Rafters | No of Rafters |  | Wt on Rafter | Wt on Rafter | Wt on Girder | Allowable | Allowable | Length of | Dist-Load on | Bend-Moment | Section | Section
R-1 | R-2 |  | R-1 | R-2 | G-1 | Stress | Stress | Girder G-1 | G-1 | For G-1 | Modulus | Modulus
# | # |  | lbs | lbs | lbs | Psi | N / m² | ft | lbs/in | lbs-in | in3 | cm3
4 | 7 |  | 1978.0079 | 2737.673 | 13537.8712 | 18000 | 124020000 | 26.24 | 42.9937 | 532850.6117 | 29.6028 | 485.1901
SELECTED SECTION |  |  | W 6 x 16
AISC STANDARD
Weight / Length |  |  | 23.8005 |  | Total Weight of Girder (Kg) |  | 762
Load / Length |  |  | 233.4824
Section Modulus |  |  | 159.3108
Bending Moment |  |  | 1867.8596
Section Modulus |  |  | 15.061
Due to the Section
Total Section Modulus |  |  | 500.251
Remarks |  |  | Not safe
COLUMN DESIGN
INPUTS
OUTPUTS
Note: | Load on Column C-2 = Load on Girder + Weight of Girder
COLUMN OF FOUR SIDED POLYGON
Load on | Wt. of |  | Total wt. on | Selected | Size of | Length of | Unit wt. | Misc. | Total wt. | Outside | Inside | Radius of | Slenderness
Girder G-1 | Girder G-1 |  | Column C-2 | Member | Member | Column |  | wt. | of Column | Diameter | Diameter | Gyration | Ratio
lbs. | lbs. |  | lbs. |  | DN | (L) feet | lbs/ft | lbs. | lbs. | (R)inches | inches | (r) inches | L/r
3
13537.8712 | 419.84 |  | 13957.7112 | 40 | 250 | 54.12 | 309.1726 | 330.75 | 31020.8838 | 10.75 | 0 | 2.6875 | 241.6521
CHECKING OF COLUMN IN COMPRESSION
See section 3.10.3.3 on page 3-44 of API - 650
If L/r < 120 then Cma= [1-(L/r)^2/34700](33000/Fs)*Y
If 120 < L/r < 131.7 then Cma= {[1-(L/r)^2/34700](33000/Fs)*Y}/[1.6*(L/200*r)]
-144.303
When L/r > 131.7 then Cma= {149000000*Y}/{(L/r)^2[1.6-(L/r*200)] | [15 empty] | -368.3647
6513.3999
Where
Cma= Max. allowable compression, in PSI
L = Unbraced length of column, in inches
r = Least radius of gyration of column, in inches
Y = 1 for structural or tubular section that have t/r value greater than or equal to 0.015
For tubular section that have t/r values < 0.015
Y = {(200/3)(t/R)}{2-(200/3)(t/R)}
t/r | Cma |  | Cinduced | Stress | Buckling
| PSI |  | PSI
2 | 6513.3999 |  | 153.7827 | Safe | Not Safe
'file:///tmp/in/input.xls'#$TANK DESIGN
CENTER COLUMN DESIGN
INPUTS
OUTPUTS
Load on | Wt. of |  | Total wt. on | Selected | Size of | Length of | Unit wt. | Misc. | Total wt. | Outside | Inside | Radius of | Slenderness
Inner rafter | inner rafter |  | Center column | Member | Member | Column |  | wt. | of Column | Diameter | Diameter | Gyration | Ratio
lbs. | lbs. |  | lbs. |  | DN | (L) feet | lbs/ft | lbs. | lbs. | (R)inches | inches | (r) inches | L/r
3
31648.1259 | 4126.24 |  | 17887.183 | 40 | 250 | 51.9224 | 309.1726 | 661.5 | 34601.6678 | 10.75 | 0 | 2.6875 | 231.8396
CHECKING OF COLUMN IN COMPRESSION
See section 3.10.3.3 on page 3-44 of API - 650
If L/r < 120 then Cma= [1-(L/r)^2/34700](33000/Fs)*Y
If 120 < L/r < 131.7 then Cma= {[1-(L/r)^2/34700](33000/Fs)*Y}/[1.6*(L/200*r)]
-133.2004
When L/r > 131.7 then Cma= {149000000*Y}/{(L/r)^2[1.6-(L/r*200)] | [15 empty] | -302.1772
6288.7947
Where
Cma= Max. allowable compression, in PSI
L = Unbraced length of column, in inches
r = Least radius of gyration of column, in inches
Y = 1 for structural or tubular section that have t/r value greater than or equal to 0.015
For tubular section that have t/r values < 0.015
Y = {(200/3)(t/R)}{2-(200/3)(t/R)}
t/r | Cma |  | Cinduced | Stress | Buckling
| PSI |  | PSI
2 | 6288.7947 |  | 197.0766 | Safe | Not Safe
DESIGN OF STEEL STORAGE TANKS AS PER API-650 (Diametet greater than 10 m but less than 20m)
Supported Cone Roof Without Column
DESIGN DATA
Service |  |  | HFO |  | Allowable Design Stress (Sd) PSI |  |  | 23200 | See Table 3-2 on page
Capacity |  |  | 2739.0761 |  | Allowable Test Stress (St) PSI |  |  | 24900 | 3-7 of API - 650
Type of tank |  |  | Supported cone roof |  | Specific Gravity of Liquid (G) |  |  | 0.96
Dia of tank (feet) |  |  | 49.2 |  | Corrosion Allowance (CA) |  |  | 0.11811 | By Client
Height of tank (feet) |  |  | 50.84
Slope of roof |  |  | 1:5
Slope of bottom |  |  | 1:100. | [6 empty] | Width | Length
[6 empty] | Full coarse Full width |  |  | A | 1219.5122 | 2439.0244
Plate Data | [5 empty] | Full coarse Partial width |  |  | B | 1219.5122 | 1859.2151
Plate width (meter) |  |  | 2.439 |  |  | Partial coarse Full width |  |  | C | 348.7805 | 2439.0244
Plate height (meter) |  |  | 1.2195 |  |  | Partial coarse Partial width |  |  | D | 348.7805 | 1859.2151
Den. of mat. (Kg/m3) |  |  | 7850
1080
INPUT | [8 empty] | 540
OUTPUT | [8 empty] | 810
SHELL
By one foot method. See sec. 3.6.3.2
on page 3-7 of API - 650
Course # | Liq. height |  | Height of | Design shell | Design shell | Hyd. shell | Adopted shell | Selected Min.
from bottom | in tank |  | each Course | thickness | thickness | thickness | thickness | shell thickness
of tank | (H) |  |  | (td) | (td) | (tt)
| ft |  | mm | inches | mm | inches | (mm) | (mm)
1 | 50.84 |  | 1219.5122 | 0.38193 | 10 | 0.25605 | 10 | 10
2 | 46.84 |  | 1219.5122 | 0.36075 | 10 | 0.2355 | 10 | 10
3 | 42.84 |  | 1219.5122 | 0.33958 | 9 | 0.21495 | 9 | 9
4 | 38.84 |  | 1219.5122 | 0.31841 | 9 | 0.1944 | 9 | 9
5 | 34.84 |  | 1219.5122 | 0.29723 | 8 | 0.17385 | 8 | 8
6 | 30.84 |  | 1219.5122 | 0.27606 | 8 | 0.1533 | 8 | 8
7 | 26.84 |  | 1219.5122 | 0.25489 | 7 | 0.13275 | 7 | 7
8 | 22.84 |  | 1219.5122 | 0.23371 | 6 | 0.1122 | 7 | 7
9 | 18.84 |  | 1219.5122 | 0.21254 | 6 | 0.09165 | 7 | 7
10 | 14.84 |  | 1219.5122 | 0.19137 | 5 | 0.071101 | 7 | 7
11 | 10.84 |  | 1219.5122 | 0.1702 | 5 | 0.050552 | 7 | 7
12 | 6.84 |  | 1219.5122 | 0.14902 | 4 | 0.030002 | 7 | 7
13 | 2.84 |  | 865.8537 | 0.12785 | 4 | 0.0094527 | 7 | 7
Note: | According to sec. 3.6.1.1 min. thk.of tank of dia. 50ft to <120ft should be 1/4 inches.
Course # | # of full |  | Size full plate |  | # of partial | Sise of Shell |  | Weight
from bottom | plates in |  | in each course |  | plates in | partial plate |  | of each
of tank | shell per |  | (Width) | (Height) | shell per | (Width) | (Height) | course
| course |  | mm | mm | course | mm | mm | Kg
1 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4511.3053 |  |  |  |  | 19.3208
2 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4511.3053 |  |  |  | ``` | 19.3208
3 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4060.1748 |  |  |  |  | 19.3208
4 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 4060.1748 |  |  |  |  | 19.3208
5 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3609.0443 |  |  |  |  | 19.3208
6 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3609.0443 |  |  |  |  | 19.3208
7 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3157.9137 |  |  |  |  | 19.3208
8 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3157.9137 |  |  |  |  | 19.3208
9 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3157.9137 |  |  |  |  | 19.3208
10 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3157.9137 |  |  |  |  | 19.3208
11 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3157.9137 |  |  |  |  | 19.3208
12 | 19 |  | 2439.0244 | 1219.5122 | 1 | 783 | 1219.5122 | 3157.9137 |  |  |  |  | 19.3208
| 0 |  | 2439.0244 | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 0 | 0 | 0 | 0 | 0
| 0 |  |  | 0 | 0 | 0 | 0 | 0
[6 empty] | Total wt. of shell plate Kg. |  | 43308.5313
BOTTOM PLATE
Accordig to sec. 3.4.1 on page 3-5 of API 650, minimum thickness of the bottom plate should be 1/4 inches without corrossion allowance,
so when we add 3mm of corrossion allowance then the bottom plate thickness comes out to be 10 mm.
Thickness of Bottom Plate |  |  | 10
Weight of Bottom Plate |  |  | 16646.5141
CURB ANGLE
See Section 3.1.5.9 ( e ) of API 650 page 3-4
Size of curb angle |  |  | 2x2x3/16
Weight of Curb Angle |  |  | 69
INTERMEDIATE WIND GIRDER (Using top course thickness)
See section 3.9.7.1 on page 3-9 of API 650
By Client
Top shell | Wind |  | Vertical | Vertical | Min. req. | Remarks
course | velocity |  | dist. b/w | dist. b/w | section
thickness |  |  | wind girder | wind girder | modulus
|  |  | & curb angle | & curb angle
(t) | (V) |  | (H1) | with 12%safety | (Z)
inches | miles/hours |  | feet | feet | inch3
0.27559 | 110 |  | 57.29 | 50.4152 | 13.8679 | Wind girder req.
0.27559 | 110 |  | 57.29 | 50.4152 | 13.8679 | Wind girder req.
'file:///tmp/in/input.xls'#$TANK DESIGN
DESIGN OF TANK ROOF. ( SUPPORTED CONE ROOF )
As per API 650 1993 Section 3.10.2 on page 3-41, Min plate thickness should be not less than 3/16" (4.76 mm).
Use 8 mm thick plate with corrosion allowance (3mm) .
Slope of Roof = 1 : |  |  | 5 | [7 empty] | m | h
INPUT
OUTPUT | [10 empty] | r | r
Radius of | Thickness of |  | Height of | Radius of | Surface area | Surface area | Weight of | Weight of | Unit load | Live load | Over lape | Total roof
Tank | Roof plate |  | roof cone | cone | of cone roof | of cone roof | roof plate | roof plate | of roof |  | of roof | load
( r ) ft | ( t ) ft |  | (h) ft | ( r ) ft | feet2 | meter2 | Kg. | lbs. | lb/ft2 | lb/ft2 | 10% | lb/ft2
24.6 | 0.026247 |  | 4.92 | 25.0872 | 1977.2129 | 183.7832 | 11544.5385 | 25455.7074 | 12.8745 | 25 | 1.2875 | 39.162
'file:///tmp/in/input.xls'#$TANK DESIGN
NUMBER OF RAFTERS
See sec. 3.10.4.5 on page 3-45 of API - 650
INPUT
OUTPUT
Note :
For the Tanks Dia greater than 10m but less than 20 m there should be two rings of Rafters.
Circumference | Min Spacing |  | Min No | Primary No. | Secondary No.
of Tank | of Rafters |  | of Rafters | of Rafters | of Rafters
(L) ft | (s) ft |  | # | # | #
154.5664 | 6.2832 |  | 24.6 | 13 | 13
As per sketch 'A'
DESIGN OF RAFTERS
INPUT
OUTPUT
SKETCH A
SECONDARY RAFTER
Length of | Area |  | No. of Rafter | Weight on each | Distri-Load | Allowable stress | Allowable stress | Bending Moment | Section | Section
Rafters |  |  | selected | Rafter | on Rafter | for bending | for bending |  | Modulus | Modulus
ft | m2 |  | # | lbs | lbs-in | Psi | N/m2 | lbs-in | in3 | cm3
14.268 | 6.4978 |  | 13 | 2737.673 | 15.9896 | 18000 | 124020000 | 58591.6775 | 3.2551 | 53.351
Rafter of Outer Ring (R-2) |  |  | I-220
Weight / Length |  |  | 31.1 |  | Total weight of
Load |  |  | 305.091 |  | Rafter (outer)(Kg) | 1759
Section Modulus |  |  | 277.8363
Bending Moment |  |  | 721.6356
Section Modulus |  |  | 5.8187
Due to the Section
Total Section Modulus |  |  | 59.1697
Remarks |  |  | Safe
Rafters are fixed at one end (Shell)and free but guided at the other end.
Uniform load over entire span.
PRIMARY RAFTER
Length of | Area |  | No. of Rafter | Weight on each | Distri-Load | Allowable stress | Allowable stress | Bending Moment | Section | Section
Rafters |  |  | selected | Rafter | on Rafter | for bending | for bending |  | Modulus | Modulus
ft | m2 |  | # | lbs | lbs/in | PSI | N/m2 | lbs-in | in3 | cm3
24.6 | 2 |  | 13 | 842.6408 | 2.8545 | 18000 | 124020000 | 41457.9278 | 2.3032 | 37.7497
Use Menu Control A - Rafter - Selection of Section
SELECTED SECTION |  |  | W 10 x 12
AISC STANDARD
Weight / Length |  |  | 17.8503 |  | Total weight of
Load |  |  | 175.1118 |  | Rafter (outer)(Kg) | 1741
Section Modulus |  |  | 178.651
Second Moment of Area |  |  | 53.8
Bending Moment |  |  | 1231.2551
Section Modulus |  |  | 9.9279
Due to the Section
Total Section Modulus |  |  | 9.9279
Remarks |  |  | Safe
Actual Stress in Rafter |  |  | 3803.4796
Remarks |  |  | Safe
Max. Allowable deflection |  |  | 20.8333
Max. Deflection at free end |  |  | 26.0893
Remarks |  |  | Not Safe
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
|  |  | 6.7623 |  |  | CURB ANGLE | Weight |  | -203.5845
|  |  | 6.7623 |  |  | 2x2x3/16 | 1.1066 |  | -958.3341
|  |  | 6.7623 |  |  | 2x2x1/4 | 1.4467 |  | 9107.3583
|  |  | 6.7623 |  |  | 3x3x3/8 | 3.2653
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
6.7623
{menucall main}
Dia<=3m | 3<Dia<=10m |  | 10<Dia<=20m | 20<Dia<=35m
{MENUCALL SHELL} | {MENUCALL main1} |  | {MENUCALL MAIN2}
Design Data | Shell & Bottom |  | Roof
{goto}saa~ | {goto}sa~ |  | {goto}ra~
Without Column | With Column
{menucall shell1} | {menucall shell2}
Design Data | Shell & Bottom |  | Roof | Rafter
{goto}sb~ | {goto}sbz~ |  | {goto}rb~ | {goto}rafter~{Menucall menuraft1}
Number of Rafter ? | Selection of Section
Select a Section
{menucall menuraft2}
Design Data | Shell |  | Roof | Rafter | Center Pole
{goto}sc~ | {goto}scz~ |  | {goto}rc~ | {goto}raftera~{Menucall menuraft3} | {goto}col1~
Number of Rafter | Selection of Section
Select a Section
{menucall menuraft4}
[12 empty] | Rafters of Outer Ring (R - 2). | Rafters of Inner Ring (R - 1). | Girder
[10 empty] | Rafters of Outer Ring (R - 2). | {R}/RV~RAFT~{R}/RV~RAFTW~{R}/RV~RAFTS~{GOTO}SELECTRAFT~ | /RVAISC~RAFTO1~ | /RVAISC~RAFTI1~ | /RVAISC~GIRD1~ | 2
[10 empty] | Rafters of Inner Ring (R - 1). | {R}/RV~RAFT2~{R}/RV~RAFTW2~{R}/RV~RAFTS2~{GOTO}SELECTRAFT2~ | /RVDIN~RAFTO1~ | /RVDIN~RAFTI1~ | /RVDIN~GIRD1~ | 3
{goto}a1~ | {goto}roof~ |  | {GOTO}RAFTER~{MENUCALL MENURAFT} | {GOTO}girder~{MENUCALL MENUgird} | {goto}column~ | {goto}cENTREPOLE~ |  |  |  | Girder | {R}/RV~gird~{R}/RV~girdW~{R}/RV~girdS~{GOTO}SELECTgird~ | /RVBS~RAFTO1~ | /RVBS~RAFTI1~ | /RVBS~GIRD1~ | 4
[12 empty] | Rafters of Outer Ring (R - 2). | Rafters of Inner Ring (R - 1). | Girder
Data Entry | Selection of Section |  | 1 |  |  |  | Data Entry | Selection of Section | 1 |  | AISC | /RVAISCA~RAFTO1~ | /RVAISCA~RAFTI1~ | /RVAISCA~GIRD1~
[6 empty] | 1 |  |  |  |  | DIN | /RVDINA~RAFTO1~ | /RVDINA~RAFTI1~ | /RVDINA~GIRD1~
| {MENUCALL RAFTO} |  | 1 |  |  |  |  | /RVGIRDER2~WHERE2~{goto}selecTGIRD~{menucall interna} | 1 |  | BS | /RVBSA~RAFTO1~ | /RVBSA~RAFTI1~ | /RVBSA~GIRD1~
|  |  |  | /RVRAFTO~WHERE2~{goto}selecTraft~{menucall interna} | /RVRAFTI~WHERE2~{goto}selecTraft2~{menucall interna} | 1
INTERNATIONAL | LOCAL
Select a rafter from International Sections Available | Select a rafter from Local Sections Available |  | * |  | DIN-CHANNEL | DIN I-BEAM
{menucall aisc} | {menucall local} |  | *
[5 empty] | {goto}DCSHAPE~{goto}DCSHAPE1~{goto}{?}~ | {goto}DISHAPE~{goto}DISHAPE1~{goto}{?}~ | 1
AISC | DIN |  | BS |  | {r}/rv~raft~{r}/rv~rafta~{r}/rv~raftaa~{r}/rv~raftaaa~{r}/rv~raftaaaa~{goto}selectraft~ | {r}/rv~raft~{r}/rv~rafta~{r}/rv~raftaa~{r}/rv~raftaaa~{r}/rv~raftaaaa~{goto}selectraft~ | 1
AISC-STANDARD | DIN-STANDARD |  | BS-STANDARD
{menucall wshapes} | {menucall dinchan}
|  |  |  | W - SHAPES | M SHAPE | AMER. STD. CHAN. | S-SHAPES
|  |  |  | {goto}WSHAPE~{goto}wSHAPE1~{goto}{?}~ | {goto}MSHAPE~{goto}MSHAPE1~{goto}{?}~ | {goto}ACSHAPE~{goto}ACSHPE2~{goto}{?}~ | {goto}SSHAPE~{goto}SSHAPE1~{goto}{?}~ | *
|  |  |  | {r}/rv~raft~{r}/rv~rafta~{r}/rv~raftaa~{r}/rv~raftaaa~{r}/rv~raftaaaa~{goto}selectraft~ | {r}/rv~raft~{r}/rv~rafta~{r}/rv~raftaa~{r}/rv~raftaaa~{r}/rv~raftaaaa~{goto}selectraft~ | {r}/rv~raft~{r}/rv~rafta~{r}/rv~raftaa~{r}/rv~raftaaa~{r}/rv~raftaaaa~{goto}selectraft~ | {r}/rv~raft~{r}/rv~rafta~{r}/rv~raftaa~{r}/rv~raftaaa~{r}/rv~raftaaaa~{goto}selectraft~ | *
|  |  |  | LOCAL CHANNEL | LOCAL GIRDER (I-BEAM) | LOCAL ANGLE
Without Column | With Column
{menucall shell3} | {menucall shell4}
|  |  |  | Design Data | Shell & Bottom | Roof | Rafter | Girder | Column | Center Column
|  |  |  | {goto}sd~ | {goto}sda~ | {goto}se~ | {menucall main3} | {menucall main4} | {goto}cola~ | {goto}colb~
|  |  |  | Data Entry | Selection of Section |  | Data Entry | Selection of Section
[5 empty] | Select a Section |  |  | Select a Section
|  |  |  | {goto}rafti~ | {menucall menuraftii} |  | {goto}gird~ | {menucall menuraft5}
[5 empty] | Rafter of Outer Ring (R-2) | Rafter of inner Ring (R-1) | 1
[5 empty] | {menucall menuraftiii} | {menucall menuraftiiii}
Design Data | Shell & Bottom |  | Roof | Rafter
{goto}bia~ | {goto}sba~ |  | {goto}sbb~ | {menucall main5}
Secondary Rafter | Primary Rafter
{menucall main6} | {menucall main7}
Data Entry | Selection Of Section |  |  | Data Entry | Selection Of Section
{goto}sbc~ | {menucall main8} |  |  | {goto}sbd~ | {menucall main9}
SECTIONS AVAILABLE
AISC - W SHAPES
S NO. | SIZE |  | Wt. (kg/m) | S (cm^3) |  | 2nd Moment of Area
1 | W 4 x 13 |  | 19.3379 | 89.4894 | AISC STANDARD | 11.3
2 | W 6 x 9 |  | 13.3878 | 91.1284 | AISC STANDARD | 16.4
3 | W 6 x 12 |  | 17.8503 | 119.8109 | AISC STANDARD | 22.1
4 | W 8 x 10 |  | 14.8753 | 128.0059 | AISC STANDARD | 30.8
5 | W 5 x 16 |  | 23.8005 | 139.4789 | AISC STANDARD | 21.3
6 | W 6 x 16 |  | 23.8005 | 159.3108 | AISC STANDARD | 32.1
7 | W 8 x 13 |  | 19.3379 | 162.4249 | AISC STANDARD | 39.6
8 | W 5 x 19 |  | 28.263 | 167.178 | AISC STANDARD | 26.2
9 | W 6 x 15 |  | 22.3129 | 167.178 | AISC STANDARD | 29.1
10 | W 10 x 12 |  | 17.8503 | 178.651 | AISC STANDARD | 53.8
11 | W 8 x 15 |  | 22.3129 | 193.402 | AISC STANDARD | 48
12 | W 6 x 20 |  | 29.7506 | 219.626 | AISC STANDARD
13 | W 10 x 15 |  | 22.3129 | 226.182 | AISC STANDARD
14 | W 8 x 18 |  | 26.7755 | 249.128 | AISC STANDARD
15 | W 10 x 17 |  | 25.288 | 265.518 | AISC STANDARD
16 | W 6 x 25 |  | 37.1882 | 273.713 | AISC STANDARD
17 | W 8 x 21 |  | 31.2381 | 298.298 | AISC STANDARD
18 | W 10 x 19 |  | 28.263 | 308.132 | AISC STANDARD
19 | W 8 x 24 |  | 35.7007 | 342.551 | AISC STANDARD
20 | W 10 x 22 |  | 32.7256 | 380.248 | AISC STANDARD
21 | W 8 x 28 |  | 41.6508 | 398.277 | AISC STANDARD
22 | W 8 x 31 |  | 46.1134 | 450.725 | AISC STANDARD
23 | W 10 x 26 |  | 38.6757 | 457.281 | AISC STANDARD
24 | W 8 x 35 |  | 52.0635 | 511.368 | AISC STANDARD
25 | W 10 x 30 |  | 44.6259 | 531.036 | AISC STANDARD
26 | W 10 x 33 |  | 49.0884 | 573.65 | AISC STANDARD
27 | W 8 x 40 |  | 59.5011 | 581.845 | AISC STANDARD
28 | W 10 x 39 |  | 58.0136 | 690.019 | AISC STANDARD
29 | W 8 x 48 |  | 71.4014 | 709.687 | AISC STANDARD
30 | W 10 x 45 |  | 66.9388 | 804.749 | AISC STANDARD
31 | W 8 x 58 |  | 86.2766 | 852.28 | AISC STANDARD
32 | W 10 x 49 |  | 72.8889 | 894.894 | AISC STANDARD
33 | W 10 x 54 |  | 80.3265 | 983.4 | AISC STANDARD
34 | W 8 x 67 |  | 99.6644 | 989.956 | AISC STANDARD
35 | W 10 x 60 |  | 89.2517 | 1093.213 | AISC STANDARD
36 | W 10 x 68 |  | 101.1519 | 1240.723 | AISC STANDARD
37 | W 10 x 77 |  | 114.5397 | 1407.901 | AISC STANDARD
38 | W 10 x 88 |  | 130.9025 | 1614.415 | AISC STANDARD
39 | W 10 x 100 |  | 148.7528 | 1835.68 | AISC STANDARD
40 | W 10 x 112 |  | 166.6032 | 2065.14 | AISC STANDARD
AISC - AMER.STD. CHANNEL
S NO. | SIZE |  | Wt. (kg/m) | S (cm^3) |  | 2nd Moment of Area
1 | C 3 x 4.1 |  | 6.0989 | 18.029 | AISC STANDARD
2 | C 3 x 5 |  | 7.4376 | 20.3236 | AISC STANDARD
3 | C 3 x 6 |  | 8.9252 | 22.6182 | AISC STANDARD
4 | C 4 x 5.4 |  | 8.0327 | 31.6327 | AISC STANDARD
5 | C 4 x 7.25 |  | 10.7846 | 37.5331 | AISC STANDARD
6 | C 5 x 6.7 |  | 9.9664 | 49.17 | AISC STANDARD
7 | C 5 x 9 |  | 13.3878 | 58.3484 | AISC STANDARD
8 | C 6 x 8.2 |  | 12.1977 | 71.7882 | AISC STANDARD
9 | C 6 x 10.5 |  | 15.619 | 82.9334 | AISC STANDARD
10 | C 6 x 13 |  | 19.3379 | 95.062 | AISC STANDARD
11 | C 7 x 9.8 |  | 14.5778 | 99.6512 | AISC STANDARD
12 | C 7 x 12.25 |  | 18.2222 | 113.5827 | AISC STANDARD
13 | C 7 x 14.775 |  | 21.941 | 127.5142 | AISC STANDARD
14 | C 8 x 11.5 |  | 17.1066 | 133.4146 | AISC STANDARD
15 | C 8 x 13.75 |  | 20.4535 | 148.0017 | AISC STANDARD
16 | C 8 x 18.75 |  | 27.8912 | 180.29 | AISC STANDARD
AISC - S-SHAPES
S NO. | SIZE |  | Wt. (kg/m) | S (cm^3) |  | 2nd Moment of Area
1 | S 3 x 5.7 |  | 8.4789 | 41.3028 | AISC STANDARD
2 | S 3 x 7.5 |  | 11.1565 | 48.0227 | AISC STANDARD
3 | S 4 x 7.7 |  | 11.454 | 99.6512 | AISC STANDARD
4 | S 4 x 9.5 |  | 14.1315 | 110.7964 | AISC STANDARD
5 | S 5 x 10 |  | 14.8753 | 201.597 | AISC STANDARD
6 | S 5 x 14.75 |  | 21.941 | 249.128 | AISC STANDARD
7 | S 6 x 12.5 |  | 18.5941 | 362.219 | AISC STANDARD
8 | S 6 x 17.25 |  | 25.6599 | 431.057 | AISC STANDARD
9 | S 7 x 15.3 |  | 22.7592 | 601.513 | AISC STANDARD
10 | S 7 x 20 |  | 29.7506 | 694.936 | AISC STANDARD
11 | S 8 x 18.4 |  | 27.3705 | 944.064 | AISC STANDARD
12 | S 8 x 23 |  | 34.2132 | 1063.711 | AISC STANDARD
AISC - M-SHAPES
S NO. | SIZE |  | Wt. (kg/m) | S (cm^3) |  | 2nd Moment of Area
1 | M 6 x 4.4 |  | 6.5451 | 39.336 | AISC STANDARD
2 | M 8 x 6.5 |  | 9.6689 | 75.7218 | AISC STANDARD
3 | M 10 x 7.5 |  | 11.1565 | 107.6823 | AISC STANDARD
4 | M 5 x 18.9 |  | 28.1143 | 157.8357 | AISC STANDARD
DIN STANDARD - CHANNEL
S NO. | SIZE |  | Wt. (kg/m) | S (cm^3) |  | 2nd Moment of Area
1 | U 30x15 |  | 0.090325 | 1.689 | DIN STANDARD
2 | U 30 x 30 |  | 0.22813 | 4.2575 | DIN STANDARD
3 | U 40 x 20 |  | 0.27062 | 3.7878 | DIN STANDARD
4 | U 40 x 40 |  | 0.50339 | 7.0458 | DIN STANDARD
5 | U 50 x 25 |  | 0.59978 | 6.726 | DIN STANDARD
6 | U 50 x 50 |  | 0.94252 | 10.5938 | DIN STANDARD
7 | U 50 x 60 |  | 1.1282 | 10.4938 | DIN STANDARD
8 | U 50 x 65 |  | 2.0528 | 17.6896 | DIN STANDARD
9 | U 50 x 80 |  | 3.7844 | 26.4844 | DIN STANDARD
10 | U 50 x 100 |  | 7.3545 | 41.1757 | DIN STANDARD
11 | U 50 x 120 |  | 12.9953 | 60.6643 | DIN STANDARD
12 | U 50 x 140 |  | 21.5994 | 86.3491 | DIN STANDARD
13 | U 50 x 160 |  | 33.0238 | 115.9317 | DIN STANDARD
14 | U 50 x 180 |  | 48.1969 | 149.9117 | DIN STANDARD
15 | U 50 x 200 |  | 68.1897 | 190.8875 | DIN STANDARD
16 | U 50 x 220 |  | 96.0368 | 244.8558 | DIN STANDARD
17 | U 50 x 240 |  | 128.5251 | 299.8234 | DIN STANDARD
18 | U 50 x 260 |  | 172.0809 | 370.7816 | DIN STANDARD
19 | U 50 x 280 |  | 224.205 | 447.7362 | DIN STANDARD
20 | U 50 x 300 |  | 286.6825 | 534.685 | DIN STANDARD
DIN STANDARD - I-BEAM
S NO. | SIZE |  | Wt. (kg/m) | S (cm^3) |  | 2nd Moment of Area
1 | I-80 |  | 5.94 | 19.4885 | DIN STANDARD
2 | I-100 |  | 8.34 | 34.1799 | DIN STANDARD
3 | I-120 |  | 11.1 | 54.6678 | DIN STANDARD
4 | I-140 |  | 14.3 | 81.8518 | DIN STANDARD
5 | I-160 |  | 17.9 | 116.9311 | DIN STANDARD
6 | I-180 |  | 21.9 | 160.9052 | DIN STANDARD
7 | I-200 |  | 26.2 | 213.874 | DIN STANDARD
8 | I-220 |  | 31.1 | 277.8363 | DIN STANDARD
9 | I-240 |  | 36.2 | 353.7916 | DIN STANDARD
10 | I-260 |  | 41.9 | 441.7398 | DIN STANDARD
11 | I-280 |  | 47.9 | 541.6809 | DIN STANDARD
12 | I-300 |  | 54.2 | 652.6155 | DIN STANDARD
13 | I-320 |  | 61 | 781.5396 | DIN STANDARD
14 | I-340 |  | 68 | 922.4566 | DIN STANDARD
15 | I-360 |  | 76.1 | 1089.3582 | DIN STANDARD
16 | I-380 |  | 84 | 1259.2581 | DIN STANDARD
17 | I-400 |  | 92.4 | 1459.1404 | DIN STANDARD
INTERNATIONAL | LOCAL
Select a rafter from International Sections Available | Select a rafter from Local Sections Available |  | 1
{menucall aisc1} | {menucall local} |  | 1
AISC | DIN |  | BS
AISC-STANDARD | DIN-STANDARD |  | BS-STANDARD
{menucall wshapes1} | {menucall dinchan1}
W - SHAPES | M SHAPE |  | AMER. STD. CHAN. | S-SHAPES |  | DIN-CHANNEL | DIN I-BEAM
{goto}WSHAPE~{goto}wSHAPE1~{goto}{?}~ | {goto}MSHAPE~{goto}MSHAPE1~{goto}{?}~ |  | {goto}ACSHAPE~{goto}ACSHPE2~{goto}{?}~ | {goto}SSHAPE~{goto}SSHAPE1~{goto}{?}~ | 1 | {goto}DCSHAPE~{goto}DCSHAPE1~{goto}{?}~ | {goto}DISHAPE~{goto}DISHAPE1~{goto}{?}~ | 1
{r}/rv~raftb~{r}/rv~raftbb~{r}/rv~raftbbb~{r}/rv~raftbbbb~{goto}selectraft1~ | {r}/rv~raftb~{r}/rv~raftbb~{r}/rv~raftbbb~{r}/rv~raftbbbb~{goto}selectraft1~ |  | {r}/rv~raftb~{r}/rv~raftbb~{r}/rv~raftbbb~{r}/rv~raftbbbb~{goto}selectraft1~ | {r}/rv~raftb~{r}/rv~raftbb~{r}/rv~raftbbb~{r}/rv~raftbbbb~{goto}selectraft1~ | 1 | {r}/rv~raftb~{r}/rv~raftbb~{r}/rv~raftbbb~{r}/rv~raftbbbb~{goto}selectraft1~ | {r}/rv~raftb~{r}/rv~raftbb~{r}/rv~raftbbb~{r}/rv~raftbbbb~{goto}selectraft1~ | 1
[11 empty] | DIN-CHANNEL | DIN I-BEAM
INTERNATIONAL | LOCAL |  |  |  |  | INTERNATIONAL | LOCAL
Select a rafter from International Sections Available | Select a rafter from Local Sections Available |  | 1 |  |  | Select a rafter from International Sections Available | Select a rafter from Local Sections Available | 1 |  |  | {goto}DCSHAPE~{goto}DCSHAPE1~{goto}{?}~ | {goto}DISHAPE~{goto}DISHAPE1~{goto}{?}~ | 1
{menucall aisc2} | {menucall local} |  | 1 |  |  | {menucall aisc3} | {menucall local} | 1 |  |  | {r}/rv~raftc~{r}/rv~raftcc~{r}/rv~raftccc~{r}/rv~raftcccc~{goto}selectraft2~ | {r}/rv~raftc~{r}/rv~raftcc~{r}/rv~raftccc~{r}/rv~raftcccc~{goto}selectraft2~ | 1
AISC | DIN |  | BS |  |  | AISC | DIN | BS
AISC-STANDARD | DIN-STANDARD |  | BS-STANDARD |  |  | AISC-STANDARD | DIN-STANDARD | BS-STANDARD
{menucall wshapes2} | {menucall dinchan2} |  |  |  |  | {menucall wshapes3} | {menucall dinchan3}
W - SHAPES | M SHAPE |  | AMER. STD. CHAN. | S-SHAPES |  | W - SHAPES | M SHAPE | AMER. STD. CHAN. | S-SHAPES |  | DIN-CHANNEL | DIN I-BEAM
{goto}WSHAPE~{goto}wSHAPE1~{goto}{?}~ | {goto}MSHAPE~{goto}MSHAPE1~{goto}{?}~ |  | {goto}ACSHAPE~{goto}ACSHPE2~{goto}{?}~ | {goto}SSHAPE~{goto}SSHAPE1~{goto}{?}~ | 1 | {goto}WSHAPE~{goto}wSHAPE1~{goto}{?}~ | {goto}MSHAPE~{goto}MSHAPE1~{goto}{?}~ | {goto}ACSHAPE~{goto}ACSHPE2~{goto}{?}~ | {goto}SSHAPE~{goto}SSHAPE1~{goto}{?}~ | 1 | {goto}DCSHAPE~{goto}DCSHAPE1~{goto}{?}~ | {goto}DISHAPE~{goto}DISHAPE1~{goto}{?}~ | 1
{r}/rv~raftc~{r}/rv~raftcc~{r}/rv~raftccc~{r}/rv~raftcccc~{goto}selectraft2~ | {r}/rv~raftc~{r}/rv~raftcc~{r}/rv~raftccc~{r}/rv~raftcccc~{goto}selectraft2~ |  | {r}/rv~raftc~{r}/rv~raftcc~{r}/rv~raftccc~{r}/rv~raftcccc~{goto}selectraft2~ | {r}/rv~raftc~{r}/rv~raftcc~{r}/rv~raftccc~{r}/rv~raftcccc~{goto}selectraft2~ | 1 | {r}/rv~raftd~{r}/rv~raftdd~{r}/rv~raftddd~{r}/rv~raftdddd~{goto}selectraft3~ | {r}/rv~raftd~{r}/rv~raftdd~{r}/rv~raftddd~{r}/rv~raftdddd~{goto}selectraft3~ | {r}/rv~raftd~{r}/rv~raftdd~{r}/rv~raftddd~{r}/rv~raftdddd~{goto}selectraft3~ | {r}/rv~raftd~{r}/rv~raftdd~{r}/rv~raftddd~{r}/rv~raftdddd~{goto}selectraft3~ | 1 | {r}/rv~raftd~{r}/rv~raftdd~{r}/rv~raftddd~{r}/rv~raftdddd~{goto}selectraft3~ | {r}/rv~raftd~{r}/rv~raftdd~{r}/rv~raftddd~{r}/rv~raftdddd~{goto}selectraft3~ | 1
INTERNATIONAL | LOCAL
Select a rafter from International Sections Available | Select a rafter from Local Sections Available |  | 1 |  |  | DIN-CHANNEL | DIN I-BEAM
{menucall aisc4} | {menucall local} |  | 1
[6 empty] | {goto}DCSHAPE~{goto}DCSHAPE1~{goto}{?}~ | {goto}DISHAPE~{goto}DISHAPE1~{goto}{?}~ | 1
AISC | DIN |  | BS |  |  | {r}/rv~girda~{r}/rv~girdaa~{r}/rv~girdaaa~{r}/rv~girdaaaa~{goto}selectgird1~ | {r}/rv~girda~{r}/rv~girdaa~{r}/rv~girdaaa~{r}/rv~girdaaaa~{goto}selectgird1~ | 1
AISC-STANDARD | DIN-STANDARD |  | BS-STANDARD
{menucall wshapes4} | {menucall dinchan4}
W - SHAPES | M SHAPE |  | AMER. STD. CHAN. | S-SHAPES
{goto}WSHAPE~{goto}wSHAPE1~{goto}{?}~ | {goto}MSHAPE~{goto}MSHAPE1~{goto}{?}~ |  | {goto}ACSHAPE~{goto}ACSHPE2~{goto}{?}~ | {goto}SSHAPE~{goto}SSHAPE1~{goto}{?}~ | 1
{r}/rv~girda~{r}/rv~girdaa~{r}/rv~girdaaa~{r}/rv~girdaaaa~{goto}selectgird1~ | {r}/rv~girda~{r}/rv~girdaa~{r}/rv~girdaaa~{r}/rv~girdaaaa~{goto}selectgird1~ |  | {r}/rv~girda~{r}/rv~girdaa~{r}/rv~girdaaa~{r}/rv~girdaaaa~{goto}selectgird1~ | {r}/rv~girda~{r}/rv~girdaa~{r}/rv~girdaaa~{r}/rv~girdaaaa~{goto}selectgird1~ | 1
[11 empty] | DIN-CHANNEL | DIN I-BEAM
INTERNATIONAL | LOCAL |  |  |  |  | INTERNATIONAL | LOCAL
Select a rafter from International Sections Available | Select a rafter from Local Sections Available |  | 1 |  |  | Select a rafter from International Sections Available | Select a rafter from Local Sections Available | 1 |  |  | {goto}DCSHAPE~{goto}DCSHAPE1~{goto}{?}~ | {goto}DISHAPE~{goto}DISHAPE1~{goto}{?}~ | 1
{menucall aisc5} | {menucall local} |  | 1 |  |  | {menucall aisc6} | {menucall local} | 1 |  |  | {r}/rv~rafte~{r}/rv~raftee~{r}/rv~rafteee~{r}/rv~rafteeee~{goto}selectraft4~ | {r}/rv~rafte~{r}/rv~raftee~{r}/rv~rafteee~{r}/rv~rafteeee~{goto}selectraft4~ | 1
AISC | DIN |  | BS |  |  | AISC | DIN | BS
AISC-STANDARD | DIN-STANDARD |  | BS-STANDARD |  |  | AISC-STANDARD | DIN-STANDARD | BS-STANDARD
{menucall wshapes5} | {menucall dinchan5} |  |  |  |  | {menucall wshapes6} | {menucall dinchan6}
W - SHAPES | M SHAPE |  | AMER. STD. CHAN. | S-SHAPES |  | W - SHAPES | M SHAPE | AMER. STD. CHAN. | S-SHAPES |  | DIN-CHANNEL | DIN I-BEAM
{goto}WSHAPE~{goto}wSHAPE1~{goto}{?}~ | {goto}MSHAPE~{goto}MSHAPE1~{goto}{?}~ |  | {goto}ACSHAPE~{goto}ACSHPE2~{goto}{?}~ | {goto}SSHAPE~{goto}SSHAPE1~{goto}{?}~ | 1 | {goto}WSHAPE~{goto}wSHAPE1~{goto}{?}~ | {goto}MSHAPE~{goto}MSHAPE1~{goto}{?}~ | {goto}ACSHAPE~{goto}ACSHPE2~{goto}{?}~ | {goto}SSHAPE~{goto}SSHAPE1~{goto}{?}~ | 1 | {goto}DCSHAPE~{goto}DCSHAPE1~{goto}{?}~ | {goto}DISHAPE~{goto}DISHAPE1~{goto}{?}~ | 1
{r}/rv~rafte~{r}/rv~raftee~{r}/rv~rafteee~{r}/rv~rafteeee~{goto}selectraft4~ | {r}/rv~rafte~{r}/rv~raftee~{r}/rv~rafteee~{r}/rv~rafteeee~{goto}selectraft4~ |  | {r}/rv~rafte~{r}/rv~raftee~{r}/rv~rafteee~{r}/rv~rafteeee~{goto}selectraft4~ | {r}/rv~rafte~{r}/rv~raftee~{r}/rv~rafteee~{r}/rv~rafteeee~{goto}selectraft4~ | 1 | {r}/rv~raftf~{r}/rv~raftff~{r}/rv~raftfff~{r}/rv~raftffff~{r}/rv~raftfffff~{goto}selectraft5~ | {r}/rv~raftf~{r}/rv~raftff~{r}/rv~raftfff~{r}/rv~raftffff~{r}/rv~raftfffff~{goto}selectraft5~ | {r}/rv~raftf~{r}/rv~raftff~{r}/rv~raftfff~{r}/rv~raftffff~{r}/rv~raftfffff~{goto}selectraft5~ | {r}/rv~raftf~{r}/rv~raftff~{r}/rv~raftfff~{r}/rv~raftffff~{r}/rv~raftfffff~{goto}selectraft5~ | 1 | {r}/rv~raftf~{r}/rv~raftff~{r}/rv~raftfff~{r}/rv~raftffff~{r}/rv~raftfffff~{goto}selectraft5~ | {r}/rv~raftf~{r}/rv~raftff~{r}/rv~raftfff~{r}/rv~raftffff~{r}/rv~raftfffff~{goto}selectraft5~ | 1
DN | OD |  | 40 | 80 | 40 | 3
15 | 21.34 |  | 15.8 | 13.88 | 80 | 4
20 | 26.67 |  | 20.93 | 18.85
25 | 33.4 |  | 26.64 | 24.3
32 | 42.16 |  | 35.04 | 32.46
40 | 48.26 |  | 40.9 | 38.1
50 | 60.33 |  | 52.51 | 49.25
65 | 73.03 |  | 62.71 | 59.01
80 | 88.9 |  | 77.92 | 73.66
90 | 101.6 |  | 90.12 | 85.44
100 | 114.3 |  | 102.26 | 97.18
125 | 141.3 |  | 128.2 | 122.24
150 | 168.28 |  | 154.06 | 146.34
200 | 219.08 |  | 202.72 | 193.68
250 | 273.05 |  | 254.51 | 242.93
300 | 323.85 |  | 303.23 | 288.95
350 | 355.6 |  | 333.34 | 317.5
400 | 406.4 |  | 381 | 363.58
450 | 457.2 |  | 428.66 | 409.6
500 | 508 |  | 477.88 | 455.62
550 | 558.8 |  | - | 501.66
600 | 609.6 |  | 574.7 | 547.72

## Course Bookings (hidden)
Name | Phone | Department | Course | Level | Lunch | Vegetarian
Martin Green | 020 7123 1234 | Administration | Access | Adv | Yes | Yes
John Doe | 01234 567890 | Design | FrontPage | Intermed | Yes | No
Make a Booking

## N1&N4-3"
| NOZZLE NECK THICKNESS CALCULATION |  |  |  |  | (UG-45) |  |  |  |  | Page : | 7
| NECK THICKNESS OF |  |  | 3 | " | ( | DN | 80 | )
FOR N1, N4
| Nozzle Dimension |  | : | 88.9 | mm O/D * | 3.05 | mm thk |  | (Sch | 10S | )
| Material |  | : | A312 TP304L
From UG-45(a)
| Minimum required thickness | [12 empty] | MPATO PSI
[13 empty] | 0.00296 | 145.038
| t | = | PRo |  | + | C |  |  | P | = | 0.42931 | psi |  | 0.42931
|  |  | SE + 0.4P | [5 empty] | R | = | 1.75 | in
[9 empty] | S | = | 17100 | psi
|  | = | 4.3935e-05 | + | 0 |  |  |  | E | = | 1
[9 empty] | C | = | 0 | in
|  | = | 4.3935e-05 | in / | 0.001116 | mm |  |  | t | = | 0.19685 | in
[9 empty] | tn | = | 0.12008 | in
| From UG-45(b)(1) |  | (SHELL THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.09375 | in / | 2.3813 | mm
| From UG-45(b)(1) |  | (END PLATE THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.23622 | in / | 6 | mm
From UG-45(b)(4)
| Standard (STD) wall thk of |  |  | 3 | NB = | 0.216 | in
Min. thickness of STD wall thickness
| = | std wall thk - 12.5%std wall thk + C
| = | 0.189 | in / | 4.8006 | mm
Hence from UG-45(b)
| Smaller thickness = |  | 0.189 | in / | 4.8006 | mm
From UG-45(a)
| Required wall thickness = |  |  | 0.189 | in / | 4.8006 | mm
| Hence pipe of |  | 3 | NB | 3.05 | mm thk ( sch |  | 10S | ) is adequate
Checking for 12.5%
| 0.875 * | 3.05 | = | 2.6688 | mm > | 4.8006 | mm ( sufficient)
Checking for weld size ( UW -16 )
|  | tc | = | not less than the smaller of 0.25 in or 0.7tmin
|  |  | = | 0.7 * 0.75 | or | 0.7 * tn |  | or | 0.7 * t |  | or | 0.25
|  |  | = | 0.525 | in | 0.084055 |  | in | 0.1378 |  | in | 0.25
| Therefore, throat must not be less than |  |  |  |  | 0.1378 |  | in / | 3.5 |  | mm
| If weld size is | 0.23622 | in / |  | 6 | mm
| Actual | tc | = | 0.7 * weld size
|  |  | = | 0.16535 | in / | 4.2 |  | mm | > | 3.5 |  | mm
| Hence, weld size |  | = | 0.23622 | in / | 6 |  | mm | is satisfactory
Strength calculations for attachment welds are not required for this detail which conforms to UW-16

## PIPEDATA-3"
|  |  | DN BASE | [6 empty] | INCH BASE
|  |  | SIZE |  | DN |  | 100 |  |  | SIZE | INCH | 3
[5 empty] | INCH |  | 4 |  |  |  | DN | 80
|  |  | SCH |  |  |  | 40S |  |  | SCH |  | 10S
|  |  | OD NOZZLE |  |  |  | 114.3 |  |  | OD NOZZLE |  | 88.9
|  |  | THICKNESS |  |  |  | 6.02 | mm |  | THICKNESS |  | 3.05 | mm
|  |  | WEIGHT |  |  |  | 16.4 | kg/m |  | WEIGHT |  | 6.59 | kg/m
|  |  | 12 | (lookup for thickness column) | [5 empty] | 7
|  |  | 28 | (lookup for weight row) | [5 empty] | 24
|  |  | NOMINAL SIZE |  |  |  | OD | SCHEDULE
|  |  | DN | 1 | INCH | DN | mm | 5S | 10S | 10 | 20 | 30 | STD | 40S | 40 | 60 | XS | 80S | 80 | 100 | 120 | 140 | 160 | XXS
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
6 |  | 1/8 | 6 | 3 | 1/8 | 6 | 10.3 | - | 1.24 | - | - | - | 1.73 | 1.73 | 1.73 | - | 2.41 | 2.41 | 2.41 | - | - | - | - | -
8 | 6.5 | 1/4 |  | 4 |  |  |  | - | 0.28 | - | - | - | 0.37 | 0.36 | 0.37 | - | 0.47 | 0.48 | 0.47 | - | - | - | - | -
10 |  | 3/8 | 8 | 5 | 1/4 | 8 | 13.7 | - | 1.65 | - | - | - | 2.24 | 2.24 | 2.24 | - | 3.12 | 3.02 | 3.12 | - | - | - | - | -
15 | 8.5 | 1/2 |  | 6 |  |  |  | - | 0.51 | - | - | - | 0.63 | 0.64 | 0.63 | - | 0.8 | 0.82 | 0.8 | - | - | - | - | -
20 |  | 3/4 | 10 | 7 | 3/8 | 10 | 17.1 | - | 1.65 | - | - | - | 2.31 | 2.31 | 2.31 | - | 3.21 | 3.2 | 3.21 | - | - | - | - | -
25 | 10.5 | 1 |  | 8 |  |  |  | - | 0.64 | - | - | - | 0.84 | 0.86 | 0.84 | - | 1.1 | 1.12 | 1.1 | - | - | - | - | -
32 |  | 1 1/4 | 15 | 9 | 1/2 | 15 | 21.3 | 1.65 | 2.11 | - | - | - | 2.77 | 2.77 | 2.77 | - | 3.73 | 3.73 | 3.73 | - | - | - | 4.78 | 7.47
40 | 15.5 | 1 1/2 |  | 10 |  |  |  | 0.82 | 1.01 | - | - | - | 1.27 | 1.3 | 1.27 | - | 1.62 | 1.65 | 1.62 | - | - | - | 1.95 | 2.55
50 |  | 2 | 20 | 11 | 3/4 | 20 | 26.7 | 1.65 | 2.11 | - | - | - | 2.87 | 2.87 | 2.87 | - | 3.91 | 3.91 | 3.91 | - | - | - | 5.56 | 7.82
65 | 20.5 | 2 1/2 |  | 12 |  |  |  | 1.04 | 1.31 | - | - | - | 1.69 | 1.71 | 1.69 | - | 2.2 | 2.24 | 2.2 | - | - | - | 2.9 | 3.64
80 |  | 3 | 25 | 13 | 1 | 25 | 33.4 | 1.65 | 2.77 | - | - | - | 3.38 | 3.38 | 3.38 | - | 4.55 | 4.55 | 4.55 | - | - | - | 6.35 | 9.09
90 | 25.5 | 3 1/2 |  | 14 |  |  |  | 1.33 | 2.13 | - | - | - | 2.5 | 2.55 | 2.5 | - | 3.24 | 3.29 | 3.24 | - | - | - | 4.24 | 5.45
100 |  | 4 | 32 | 15 | 1 1/4 | 32 | 42.2 | 1.65 | 2.77 | - | - | - | 3.56 | 3.56 | 3.56 | - | 4.85 | 4.85 | 4.85 | - | - | - | 6.35 | 9.7
125 | 32.5 | 5 |  | 16 |  |  |  | 1.68 | 2.76 | - | - | - | 3.39 | 3.46 | 3.39 | - | 4.47 | 4.56 | 4.47 | - | - | - | 5.61 | 7.77
150 |  | 6 | 40 | 17 | 1 1/2 | 40 | 48.3 | 1.65 | 2.77 | - | - | - | 3.68 | 3.68 | 3.68 | - | 5.08 | 5.08 | 5.08 | - | - | - | 7.14 | 10.15
200 | 40.5 | 8 |  | 18 |  |  |  | 1.95 | 3.1 | - | - | - | 4.05 | 4.13 | 4.05 | - | 5.41 | 5.51 | 5.41 | - | - | - | 7.25 | 9.56
250 |  | 10 | 50 | 19 | 2 | 50 | 60.3 | 1.65 | 2.77 | - | - | - | 3.91 | 3.91 | 3.91 | - | 5.54 | 5.54 | 5.54 | - | - | - | 8.74 | 11.07
300 | 50.5 | 12 |  | 20 |  |  |  | 2.44 | 4.01 | - | - | - | 5.44 | 5.54 | 5.44 | - | 7.48 | 7.63 | 7.48 | - | - | - | 11.11 | 13.14
350 |  | 14 | 65 | 21 | 2 1/2 | 65 | 73 | 2.11 | 3.05 | - | - | - | 5.16 | 5.16 | 5.16 | - | 7.01 | 7.01 | 7.01 | - | - | - | 9.53 | 14.02
400 | 65.5 | 16 |  | 22 |  |  |  | 3.77 | 5.36 | - | - | - | 8.63 | 8.81 | 8.63 | - | 11.41 | 11.64 | 11.41 | - | - | - | 14.92 | 20.39
450 |  | 18 | 80 | 23 | 3 | 80 | 88.9 | 2.11 | 3.05 | - | - | - | 5.49 | 5.49 | 5.49 | - | 7.62 | 7.62 | 7.62 | - | - | - | 11.13 | 15.24
500 | 80.5 | 20 |  | 24 |  |  |  | 4.6 | 6.59 | - | - | - | 11.29 | 11.52 | 11.29 | - | 15.27 | 15.59 | 15.27 | - | - | - | 21.35 | 27.68
550 |  | 22 | 90 | 25 | 3 1/2 | 90 | 101.6 | 2.11 | 3.05 | - | - | - | 5.74 | 5.74 | 5.74 | - | 8.08 | 8.08 | 8.08 | - | - | - | - | -
600 | 90.5 | 24 |  | 26 |  |  |  | 5.29 | 7.55 | - | - | - | 13.57 | 13.84 | 13.57 | - | 18.63 | 19.01 | 18.63 | - | - | - | - | -
650 |  | 26 | 100 | 27 | 4 | 100 | 114.3 | 2.11 | 3.05 | - | - | - | 6.02 | 6.02 | 6.02 | - | 8.56 | 8.56 | 8.56 | - | 11.13 | - | 13.49 | 17.12
700 | 100.5 | 28 |  | 28 |  |  |  | 5.96 | 8.52 | - | - | - | 16.07 | 16.4 | 16.07 | - | 22.32 | 22.77 | 22.32 | - | 28.32 | - | 33.54 | 41.03
750 |  | 30 | 125 | 29 | 5 | 125 | 141.3 | 2.77 | 3.4 | - | - | - | 6.55 | 6.55 | 6.55 | - | 9.53 | 9.53 | 9.53 | - | 12.7 | - | 15.88 | 19.05
800 | 125.5 | 32 |  | 30 |  |  |  | 9.67 | 11.82 | - | - | - | 21.77 | 22.2 | 21.77 | - | 30.97 | 31.59 | 30.97 | - | 40.28 | - | 49.11 | 57.43
850 |  | 34 | 150 | 31 | 6 | 150 | 168.3 | 2.77 | 3.4 | - | - | - | 7.11 | 7.11 | 7.11 | - | 10.97 | 10.97 | 10.97 | - | 14.27 | - | 18.26 | 21.95
900 | 150.5 | 36 |  | 32 |  |  |  | 11.55 | 14.13 | - | - | - | 28.26 | 28.83 | 28.26 | - | 42.56 | 43.42 | 42.56 | - | 54.2 | - | 67.56 | 79.22
950 |  | 38 | 200 | 33 | 8 | 200 | 219.1 | 2.77 | 3.76 | - | 6.35 | 7.04 | 8.18 | 8.18 | 8.18 | 10.31 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 22.23
1000 | 200.5 | 40 |  | 34 |  |  |  | 15.09 | 20.37 | - | 33.31 | 36.81 | 42.55 | 43.39 | 42.55 | 53.08 | 64.64 | 65.95 | 64.64 | 75.92 | 90.44 | 100.92 | 111.27 | 107.92
1050 |  | 42 | 250 | 35 | 10 | 250 | 273.1 | 3.4 | 4.19 | - | 6.35 | 7.8 | 9.27 | 9.27 | 9.27 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 25.4
1100 | 250.5 | 44 |  | 36 |  |  |  | 23.08 | 28.34 | - | 41.77 | 51.03 | 60.31 | 61.52 | 60.31 | 81.55 | 81.55 | 83.19 | 96.01 | 114.75 | 133.06 | 155.15 | 172.33 | 155.15
1150 |  | 46 | 300 | 37 | 12 | 300 | 323.9 | 3.96 | 4.57 | - | 6.35 | 8.38 | 9.53 | 9.52 | 10.31 | 14.27 | 12.7 | 12.7 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 25.4
1200 | 300.5 | 48 |  | 38 |  |  |  | 31.89 | 36.73 | - | 49.73 | 65.2 | 73.88 | 75.32 | 79.73 | 108.96 | 97.46 | 99.43 | 132.08 | 159.91 | 186.75 | 208.14 | 238.76 | 186.97
|  |  | 350 | 39 | 14 | 350 | 355.6 | 3.96 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 11.13 | 15.09 | 12.7 | - | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | -
| 350.5 |  |  | 40 |  |  |  | 35.06 | 42.14 | 54.69 | 67.9 | 81.33 | 81.33 | - | 94.55 | 12.71 | 107.39 | - | 158.1 | 194.96 | 224.65 | 253.56 | 281.7 | -
|  |  | 400 | 41 | 16 | 400 | 406.4 | 4.19 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 12.7 | 16.66 | 12.7 | - | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | -
| 400.5 |  |  | 42 |  |  |  | 42.41 | 48.26 | 62.64 | 77.83 | 93.27 | 93.27 | - | 123.3 | 160.12 | 123.3 | - | 203.53 | 245.56 | 286.64 | 333.19 | 365.35 | -
|  |  | 450 | 43 | 18 | 450 | 457.2 | 4.19 | 4.78 | 6.35 | 7.92 | 11.13 | 9.53 | - | 14.27 | 19.05 | 12.7 | - | 23.88 | 29.36 | 34.93 | 39.67 | 45.34 | -
| 450.5 |  |  | 44 |  |  |  | 47.77 | 54.36 | 70.57 | 87.71 | 122.38 | 105.16 | - | 155.8 | 205.74 | 139.15 | - | 254.55 | 309.62 | 363.56 | 408.26 | 459.37 | -
|  |  | 500 | 45 | 20 | 500 | 508 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | 15.09 | 20.62 | 12.7 | - | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | -
| 500.5 |  |  | 46 |  |  |  | 60.46 | 70 | 78.55 | 117.15 | 155.12 | 117.15 | - | 173.42 | 247.83 | 155.12 | - | 311.17 | 381.53 | 441.49 | 508.11 | 564.81 | -
|  |  | 550 | 47 | 22 | 550 | 558.8 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | - | 22.23 | 12.7 | - | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | -
| 550.5 |  |  | 48 |  |  |  | 66.57 | 77.06 | 86.54 | 127.13 | 171.09 | 129.13 | - | - | 294.25 | 171.09 | - | 373.83 | 451.42 | 527.02 | 600.63 | 672.26 | -
|  |  | 600 | 49 | 24 | 600 | 609.8 | 5.54 | 6.35 | 6.35 | 9.53 | 14.27 | 9.53 | - | 17.48 | 24.61 | 12.7 | - | 30.96 | 39.89 | 46.02 | 52.37 | 59.54 | -
| 600.5 |  |  | 50 |  |  |  | 84.16 | 96.37 | 94.53 | 141.12 | 209.64 | 141.12 | - | 255.41 | 355.26 | 187.06 | - | 442.08 | 547.71 | 640.03 | 720.16 | 808.22 | -
|  |  | 650 | 51 | 26 | 650 | 660.4 | - | - | 7.92 | 12.7 | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 650.5 |  |  | 52 |  |  |  | - | - | 127.36 | 202.72 | - | 152.87 | - | - | - | 202.72 | - | - | - | - | - | - | -
|  |  | 700 | 53 | 28 | 700 | 711.2 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 700.5 |  |  | 54 |  |  |  | - | - | 137.32 | 218.69 | 271.21 | 164.87 | - | - | - | 218.69 | - | - | - | - | - | - | -
|  |  | 750 | 55 | 30 | 750 | 762 | 6.35 | 7.92 | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 750.5 |  |  | 56 |  |  |  | 120.72 | 150.36 | 147.28 | 234.67 | 292.18 | 176.84 | - | - | - | 234.67 | - | - | - | - | - | - | -
|  |  | 800 | 57 | 32 | 800 | 812.8 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 800.5 |  |  | 58 |  |  |  | - | - | 157.24 | 250.64 | 312.15 | 188.82 | - | 342.91 | - | 250.64 | - | - | - | - | - | - | -
|  |  | 850 | 59 | 34 | 850 | 863.6 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 850.5 |  |  | 60 |  |  |  | - | - | 167.2 | 266.61 | 332.12 | 200.31 | - | 364.9 | - | 266.61 | - | - | - | - | - | - | -
|  |  | 900 | 61 | 36 | 900 | 914.4 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 19.05 | - | 12.7 | - | - | - | - | - | - | -
| 900.5 |  |  | 62 |  |  |  | - | - | 176.96 | 282.27 | 351.7 | 212.56 | - | 420.4 | - | 282.27 | - | - | - | - | - | - | -
|  |  | 950 | 63 | 38 | 950 | 965.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 950.5 |  |  | 64 |  |  |  | - | - | - | - | - | 224.54 | - | - | - | 298.24 | - | - | - | - | - | - | -
|  |  | 1000 | 65 | 40 | 1000 | 1016 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1000.5 |  |  | 66 |  |  |  | - | - | - | - | - | 236.53 | - | - | - | 314.22 | - | - | - | - | - | - | -
|  |  | 1050 | 67 | 42 | 1050 | 1066.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1050.5 |  |  | 68 |  |  |  | - | - | - | - | - | 248.53 | - | - | - | 330.19 | - | - | - | - | - | - | -
|  |  | 1100 | 69 | 44 | 1100 | 1117.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1100.5 |  |  | 70 |  |  |  | - | - | - | - | - | 260.5 | - | - | - | 346.16 | - | - | - | - | - | - | -
|  |  | 1150 | 71 | 46 | 1150 | 1168.4 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1150.5 |  |  | 72 |  |  |  | - | - | - | - | - | 272.25 | - | - | - | 351.82 | - | - | - | - | - | - | -
|  |  | 1200 | 73 | 48 | 1200 | 1219.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1200.5 |  |  | 74 |  |  |  | - | - | - | - | - | 284.24 | - | - | - | 377.79 | - | - | - | - | - | - | -
Available for stainless steel
Available for carbon steel

## N2&N3-4"
| NOZZLE NECK THICKNESS CALCULATION |  |  |  |  | (UG-45) |  |  |  |  | Page : | 8
| NECK THICKNESS OF |  |  | 4 | " | ( | DN | 100 | )
FOR N2, N3
| Nozzle Dimension |  | : | 114.3 | mm O/D * | 3.05 | mm thk |  | (Sch | 10S | )
| Material |  | : | A312 TP304
From UG-45(a)
| Minimum required thickness | [12 empty] | MPATO PSI
[13 empty] | 0.00296 | 145.038
| t | = | PRo |  | + | C |  |  | P | = | 0.42931 | psi |  | 0.42931
|  |  | SE + 0.4P | [5 empty] | R | = | 2.25 | in
[9 empty] | S | = | 17100 | psi
|  | = | 5.6488e-05 | + | 0 |  |  |  | E | = | 1 |  |  | 5.6488e-05
[9 empty] | C | = | 0 | in
|  | = | 5.6488e-05 | in / | 0.0014348 | mm |  |  | t | = | 0.19685 | in
[9 empty] | tn | = | 0.12008 | in
| From UG-45(b)(1) |  | (SHELL THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.09375 | in / | 2.3813 | mm
| From UG-45(b)(1) |  | (END PLATE THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.23622 | in / | 6 | mm
From UG-45(b)(4)
| Standard (STD) wall thk of |  |  | 4 | NB = | 0.216 | in
Min. thickness of STD wall thickness
| = | std wall thk - 12.5%std wall thk + C
| = | 0.189 | in / | 4.8006 | mm
Hence from UG-45(b)
| Smaller thickness = |  | 0.189 | in / | 4.8006 | mm
From UG-45(a)
| Required wall thickness = |  |  | 0.189 | in / | 4.8006 | mm
| Hence pipe of |  | 4 | NB | 3.05 | mm thk ( sch |  | 10S | ) is adequate
Checking for 12.5%
| 0.875 * | 3.05 | = | 2.6688 | mm > | 4.8006 | mm ( sufficient)
Checking for weld size ( UW -16 )
|  | tc | = | not less than the smaller of 0.25 in or 0.7tmin
|  |  | = | 0.7 * 0.75 | or | 0.7 * tn |  | or | 0.7 * t |  | or | 0.25
|  |  | = | 0.525 | in | 0.084055 |  | in | 0.1378 |  | in | 0.25
| Therefore, throat must not be less than |  |  |  |  | 0.1378 |  | in / | 3.5 |  | mm
| If weld size is | 0.23622 | in / |  | 6 | mm
| Actual | tc | = | 0.7 * weld size
|  |  | = | 0.16535 | in / | 4.2 |  | mm | > | 3.5 |  | mm
| Hence, weld size |  | = | 0.23622 | in / | 6 |  | mm | is satisfactory
Strength calculations for attachment welds are not required for this detail which conforms to UW-16

## PIPEDATA-4"
|  |  | DN BASE | [6 empty] | INCH BASE
|  |  | SIZE |  | DN |  | 100 |  |  | SIZE | INCH | 4
[5 empty] | INCH |  | 4 |  |  |  | DN | 100
|  |  | SCH |  |  |  | 40S |  |  | SCH |  | 10S
|  |  | OD NOZZLE |  |  |  | 114.3 |  |  | OD NOZZLE |  | 114.3
|  |  | THICKNESS |  |  |  | 6.02 | mm |  | THICKNESS |  | 3.05 | mm
|  |  | WEIGHT |  |  |  | 16.4 | kg/m |  | WEIGHT |  | 8.52 | kg/m
|  |  | 12 | (lookup for thickness column) | [5 empty] | 7
|  |  | 28 | (lookup for weight row) | [5 empty] | 28
|  |  | NOMINAL SIZE |  |  |  | OD | SCHEDULE
|  |  | DN | 1 | INCH | DN | mm | 5S | 10S | 10 | 20 | 30 | STD | 40S | 40 | 60 | XS | 80S | 80 | 100 | 120 | 140 | 160 | XXS
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
6 |  | 1/8 | 6 | 3 | 1/8 | 6 | 10.3 | - | 1.24 | - | - | - | 1.73 | 1.73 | 1.73 | - | 2.41 | 2.41 | 2.41 | - | - | - | - | -
8 | 6.5 | 1/4 |  | 4 |  |  |  | - | 0.28 | - | - | - | 0.37 | 0.36 | 0.37 | - | 0.47 | 0.48 | 0.47 | - | - | - | - | -
10 |  | 3/8 | 8 | 5 | 1/4 | 8 | 13.7 | - | 1.65 | - | - | - | 2.24 | 2.24 | 2.24 | - | 3.12 | 3.02 | 3.12 | - | - | - | - | -
15 | 8.5 | 1/2 |  | 6 |  |  |  | - | 0.51 | - | - | - | 0.63 | 0.64 | 0.63 | - | 0.8 | 0.82 | 0.8 | - | - | - | - | -
20 |  | 3/4 | 10 | 7 | 3/8 | 10 | 17.1 | - | 1.65 | - | - | - | 2.31 | 2.31 | 2.31 | - | 3.21 | 3.2 | 3.21 | - | - | - | - | -
25 | 10.5 | 1 |  | 8 |  |  |  | - | 0.64 | - | - | - | 0.84 | 0.86 | 0.84 | - | 1.1 | 1.12 | 1.1 | - | - | - | - | -
32 |  | 1 1/4 | 15 | 9 | 1/2 | 15 | 21.3 | 1.65 | 2.11 | - | - | - | 2.77 | 2.77 | 2.77 | - | 3.73 | 3.73 | 3.73 | - | - | - | 4.78 | 7.47
40 | 15.5 | 1 1/2 |  | 10 |  |  |  | 0.82 | 1.01 | - | - | - | 1.27 | 1.3 | 1.27 | - | 1.62 | 1.65 | 1.62 | - | - | - | 1.95 | 2.55
50 |  | 2 | 20 | 11 | 3/4 | 20 | 26.7 | 1.65 | 2.11 | - | - | - | 2.87 | 2.87 | 2.87 | - | 3.91 | 3.91 | 3.91 | - | - | - | 5.56 | 7.82
65 | 20.5 | 2 1/2 |  | 12 |  |  |  | 1.04 | 1.31 | - | - | - | 1.69 | 1.71 | 1.69 | - | 2.2 | 2.24 | 2.2 | - | - | - | 2.9 | 3.64
80 |  | 3 | 25 | 13 | 1 | 25 | 33.4 | 1.65 | 2.77 | - | - | - | 3.38 | 3.38 | 3.38 | - | 4.55 | 4.55 | 4.55 | - | - | - | 6.35 | 9.09
90 | 25.5 | 3 1/2 |  | 14 |  |  |  | 1.33 | 2.13 | - | - | - | 2.5 | 2.55 | 2.5 | - | 3.24 | 3.29 | 3.24 | - | - | - | 4.24 | 5.45
100 |  | 4 | 32 | 15 | 1 1/4 | 32 | 42.2 | 1.65 | 2.77 | - | - | - | 3.56 | 3.56 | 3.56 | - | 4.85 | 4.85 | 4.85 | - | - | - | 6.35 | 9.7
125 | 32.5 | 5 |  | 16 |  |  |  | 1.68 | 2.76 | - | - | - | 3.39 | 3.46 | 3.39 | - | 4.47 | 4.56 | 4.47 | - | - | - | 5.61 | 7.77
150 |  | 6 | 40 | 17 | 1 1/2 | 40 | 48.3 | 1.65 | 2.77 | - | - | - | 3.68 | 3.68 | 3.68 | - | 5.08 | 5.08 | 5.08 | - | - | - | 7.14 | 10.15
200 | 40.5 | 8 |  | 18 |  |  |  | 1.95 | 3.1 | - | - | - | 4.05 | 4.13 | 4.05 | - | 5.41 | 5.51 | 5.41 | - | - | - | 7.25 | 9.56
250 |  | 10 | 50 | 19 | 2 | 50 | 60.3 | 1.65 | 2.77 | - | - | - | 3.91 | 3.91 | 3.91 | - | 5.54 | 5.54 | 5.54 | - | - | - | 8.74 | 11.07
300 | 50.5 | 12 |  | 20 |  |  |  | 2.44 | 4.01 | - | - | - | 5.44 | 5.54 | 5.44 | - | 7.48 | 7.63 | 7.48 | - | - | - | 11.11 | 13.14
350 |  | 14 | 65 | 21 | 2 1/2 | 65 | 73 | 2.11 | 3.05 | - | - | - | 5.16 | 5.16 | 5.16 | - | 7.01 | 7.01 | 7.01 | - | - | - | 9.53 | 14.02
400 | 65.5 | 16 |  | 22 |  |  |  | 3.77 | 5.36 | - | - | - | 8.63 | 8.81 | 8.63 | - | 11.41 | 11.64 | 11.41 | - | - | - | 14.92 | 20.39
450 |  | 18 | 80 | 23 | 3 | 80 | 88.9 | 2.11 | 3.05 | - | - | - | 5.49 | 5.49 | 5.49 | - | 7.62 | 7.62 | 7.62 | - | - | - | 11.13 | 15.24
500 | 80.5 | 20 |  | 24 |  |  |  | 4.6 | 6.59 | - | - | - | 11.29 | 11.52 | 11.29 | - | 15.27 | 15.59 | 15.27 | - | - | - | 21.35 | 27.68
550 |  | 22 | 90 | 25 | 3 1/2 | 90 | 101.6 | 2.11 | 3.05 | - | - | - | 5.74 | 5.74 | 5.74 | - | 8.08 | 8.08 | 8.08 | - | - | - | - | -
600 | 90.5 | 24 |  | 26 |  |  |  | 5.29 | 7.55 | - | - | - | 13.57 | 13.84 | 13.57 | - | 18.63 | 19.01 | 18.63 | - | - | - | - | -
650 |  | 26 | 100 | 27 | 4 | 100 | 114.3 | 2.11 | 3.05 | - | - | - | 6.02 | 6.02 | 6.02 | - | 8.56 | 8.56 | 8.56 | - | 11.13 | - | 13.49 | 17.12
700 | 100.5 | 28 |  | 28 |  |  |  | 5.96 | 8.52 | - | - | - | 16.07 | 16.4 | 16.07 | - | 22.32 | 22.77 | 22.32 | - | 28.32 | - | 33.54 | 41.03
750 |  | 30 | 125 | 29 | 5 | 125 | 141.3 | 2.77 | 3.4 | - | - | - | 6.55 | 6.55 | 6.55 | - | 9.53 | 9.53 | 9.53 | - | 12.7 | - | 15.88 | 19.05
800 | 125.5 | 32 |  | 30 |  |  |  | 9.67 | 11.82 | - | - | - | 21.77 | 22.2 | 21.77 | - | 30.97 | 31.59 | 30.97 | - | 40.28 | - | 49.11 | 57.43
850 |  | 34 | 150 | 31 | 6 | 150 | 168.3 | 2.77 | 3.4 | - | - | - | 7.11 | 7.11 | 7.11 | - | 10.97 | 10.97 | 10.97 | - | 14.27 | - | 18.26 | 21.95
900 | 150.5 | 36 |  | 32 |  |  |  | 11.55 | 14.13 | - | - | - | 28.26 | 28.83 | 28.26 | - | 42.56 | 43.42 | 42.56 | - | 54.2 | - | 67.56 | 79.22
950 |  | 38 | 200 | 33 | 8 | 200 | 219.1 | 2.77 | 3.76 | - | 6.35 | 7.04 | 8.18 | 8.18 | 8.18 | 10.31 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 22.23
1000 | 200.5 | 40 |  | 34 |  |  |  | 15.09 | 20.37 | - | 33.31 | 36.81 | 42.55 | 43.39 | 42.55 | 53.08 | 64.64 | 65.95 | 64.64 | 75.92 | 90.44 | 100.92 | 111.27 | 107.92
1050 |  | 42 | 250 | 35 | 10 | 250 | 273.1 | 3.4 | 4.19 | - | 6.35 | 7.8 | 9.27 | 9.27 | 9.27 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 25.4
1100 | 250.5 | 44 |  | 36 |  |  |  | 23.08 | 28.34 | - | 41.77 | 51.03 | 60.31 | 61.52 | 60.31 | 81.55 | 81.55 | 83.19 | 96.01 | 114.75 | 133.06 | 155.15 | 172.33 | 155.15
1150 |  | 46 | 300 | 37 | 12 | 300 | 323.9 | 3.96 | 4.57 | - | 6.35 | 8.38 | 9.53 | 9.52 | 10.31 | 14.27 | 12.7 | 12.7 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 25.4
1200 | 300.5 | 48 |  | 38 |  |  |  | 31.89 | 36.73 | - | 49.73 | 65.2 | 73.88 | 75.32 | 79.73 | 108.96 | 97.46 | 99.43 | 132.08 | 159.91 | 186.75 | 208.14 | 238.76 | 186.97
|  |  | 350 | 39 | 14 | 350 | 355.6 | 3.96 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 11.13 | 15.09 | 12.7 | - | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | -
| 350.5 |  |  | 40 |  |  |  | 35.06 | 42.14 | 54.69 | 67.9 | 81.33 | 81.33 | - | 94.55 | 12.71 | 107.39 | - | 158.1 | 194.96 | 224.65 | 253.56 | 281.7 | -
|  |  | 400 | 41 | 16 | 400 | 406.4 | 4.19 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 12.7 | 16.66 | 12.7 | - | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | -
| 400.5 |  |  | 42 |  |  |  | 42.41 | 48.26 | 62.64 | 77.83 | 93.27 | 93.27 | - | 123.3 | 160.12 | 123.3 | - | 203.53 | 245.56 | 286.64 | 333.19 | 365.35 | -
|  |  | 450 | 43 | 18 | 450 | 457.2 | 4.19 | 4.78 | 6.35 | 7.92 | 11.13 | 9.53 | - | 14.27 | 19.05 | 12.7 | - | 23.88 | 29.36 | 34.93 | 39.67 | 45.34 | -
| 450.5 |  |  | 44 |  |  |  | 47.77 | 54.36 | 70.57 | 87.71 | 122.38 | 105.16 | - | 155.8 | 205.74 | 139.15 | - | 254.55 | 309.62 | 363.56 | 408.26 | 459.37 | -
|  |  | 500 | 45 | 20 | 500 | 508 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | 15.09 | 20.62 | 12.7 | - | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | -
| 500.5 |  |  | 46 |  |  |  | 60.46 | 70 | 78.55 | 117.15 | 155.12 | 117.15 | - | 173.42 | 247.83 | 155.12 | - | 311.17 | 381.53 | 441.49 | 508.11 | 564.81 | -
|  |  | 550 | 47 | 22 | 550 | 558.8 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | - | 22.23 | 12.7 | - | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | -
| 550.5 |  |  | 48 |  |  |  | 66.57 | 77.06 | 86.54 | 127.13 | 171.09 | 129.13 | - | - | 294.25 | 171.09 | - | 373.83 | 451.42 | 527.02 | 600.63 | 672.26 | -
|  |  | 600 | 49 | 24 | 600 | 609.8 | 5.54 | 6.35 | 6.35 | 9.53 | 14.27 | 9.53 | - | 17.48 | 24.61 | 12.7 | - | 30.96 | 39.89 | 46.02 | 52.37 | 59.54 | -
| 600.5 |  |  | 50 |  |  |  | 84.16 | 96.37 | 94.53 | 141.12 | 209.64 | 141.12 | - | 255.41 | 355.26 | 187.06 | - | 442.08 | 547.71 | 640.03 | 720.16 | 808.22 | -
|  |  | 650 | 51 | 26 | 650 | 660.4 | - | - | 7.92 | 12.7 | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 650.5 |  |  | 52 |  |  |  | - | - | 127.36 | 202.72 | - | 152.87 | - | - | - | 202.72 | - | - | - | - | - | - | -
|  |  | 700 | 53 | 28 | 700 | 711.2 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 700.5 |  |  | 54 |  |  |  | - | - | 137.32 | 218.69 | 271.21 | 164.87 | - | - | - | 218.69 | - | - | - | - | - | - | -
|  |  | 750 | 55 | 30 | 750 | 762 | 6.35 | 7.92 | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 750.5 |  |  | 56 |  |  |  | 120.72 | 150.36 | 147.28 | 234.67 | 292.18 | 176.84 | - | - | - | 234.67 | - | - | - | - | - | - | -
|  |  | 800 | 57 | 32 | 800 | 812.8 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 800.5 |  |  | 58 |  |  |  | - | - | 157.24 | 250.64 | 312.15 | 188.82 | - | 342.91 | - | 250.64 | - | - | - | - | - | - | -
|  |  | 850 | 59 | 34 | 850 | 863.6 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 850.5 |  |  | 60 |  |  |  | - | - | 167.2 | 266.61 | 332.12 | 200.31 | - | 364.9 | - | 266.61 | - | - | - | - | - | - | -
|  |  | 900 | 61 | 36 | 900 | 914.4 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 19.05 | - | 12.7 | - | - | - | - | - | - | -
| 900.5 |  |  | 62 |  |  |  | - | - | 176.96 | 282.27 | 351.7 | 212.56 | - | 420.4 | - | 282.27 | - | - | - | - | - | - | -
|  |  | 950 | 63 | 38 | 950 | 965.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 950.5 |  |  | 64 |  |  |  | - | - | - | - | - | 224.54 | - | - | - | 298.24 | - | - | - | - | - | - | -
|  |  | 1000 | 65 | 40 | 1000 | 1016 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1000.5 |  |  | 66 |  |  |  | - | - | - | - | - | 236.53 | - | - | - | 314.22 | - | - | - | - | - | - | -
|  |  | 1050 | 67 | 42 | 1050 | 1066.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1050.5 |  |  | 68 |  |  |  | - | - | - | - | - | 248.53 | - | - | - | 330.19 | - | - | - | - | - | - | -
|  |  | 1100 | 69 | 44 | 1100 | 1117.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1100.5 |  |  | 70 |  |  |  | - | - | - | - | - | 260.5 | - | - | - | 346.16 | - | - | - | - | - | - | -
|  |  | 1150 | 71 | 46 | 1150 | 1168.4 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1150.5 |  |  | 72 |  |  |  | - | - | - | - | - | 272.25 | - | - | - | 351.82 | - | - | - | - | - | - | -
|  |  | 1200 | 73 | 48 | 1200 | 1219.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1200.5 |  |  | 74 |  |  |  | - | - | - | - | - | 284.24 | - | - | - | 377.79 | - | - | - | - | - | - | -
Available for stainless steel
Available for carbon steel

## N2-0.5"
| NOZZLE NECK THICKNESS CALCULATION |  |  |  |  | (UG-45) |  |  |  |  | Page : | 9
| NECK THICKNESS OF |  |  | 1/2 | " | ( | DN | 15 | )
FOR N5
| Nozzle Dimension |  | : | 21.3 | mm O/D * | 2.11 | mm thk |  | (Sch | 10S | )
| Material |  | : | A312 TP304
From UG-45(a)
| Minimum required thickness | [12 empty] | MPATO PSI
[13 empty] | 0.00296 | 145.038
| t | = | PRo |  | + | C |  |  | P | = | 0.42931 | psi |  | 0.42931
|  |  | SE + 0.4P | [5 empty] | R | = | 0.41929 | in
[9 empty] | S | = | 17100 | psi
|  | = | 1.0527e-05 | + | 0 |  |  |  | E | = | 1
[9 empty] | C | = | 0 | in
|  | = | 1.0527e-05 | in / | 0.00026738 | mm |  |  | t | = | 0.19685 | in
[9 empty] | tn | = | 0.083071 | in
| From UG-45(b)(1) |  | (SHELL THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.09375 | in / | 2.3813 | mm
| From UG-45(b)(1) |  | (END PLATE THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.23622 | in / | 6 | mm
From UG-45(b)(4)
| Standard (STD) wall thk of |  |  | 1/2 | NB = | 0.216 | in
Min. thickness of STD wall thickness
| = | std wall thk - 12.5%std wall thk + C
| = | 0.189 | in / | 4.8006 | mm
Hence from UG-45(b)
| Smaller thickness = |  | 0.189 | in / | 4.8006 | mm
From UG-45(a)
| Required wall thickness = |  |  | 0.189 | in / | 4.8006 | mm
| Hence pipe of |  | 1/2 | NB | 2.11 | mm thk ( sch |  | 10S | ) is adequate
Checking for 12.5%
| 0.875 * | 2.11 | = | 1.8462 | mm > | 4.8006 | mm ( sufficient)
Checking for weld size ( UW -16 )
|  | tc | = | not less than the smaller of 0.25 in or 0.7tmin
|  |  | = | 0.7 * 0.75 | or | 0.7 * tn |  | or | 0.7 * t |  | or | 0.25
|  |  | = | 0.525 | in | 0.05815 |  | in | 0.1378 |  | in | 0.25
| Therefore, throat must not be less than |  |  |  |  | 0.1378 |  | in / | 3.5 |  | mm
| If weld size is | 0.23622 | in / |  | 6 | mm
| Actual | tc | = | 0.7 * weld size
|  |  | = | 0.16535 | in / | 4.2 |  | mm | > | 3.5 |  | mm
| Hence, weld size |  | = | 0.23622 | in / | 6 |  | mm | is satisfactory
Strength calculations for attachment welds are not required for this detail which conforms to UW-16

## PIPEDATA-0.5"
|  |  | DN BASE | [6 empty] | INCH BASE
|  |  | SIZE |  | DN |  | 15 |  |  | SIZE | INCH | 1/2
[5 empty] | INCH |  | 1/2 |  |  |  | DN | 15
|  |  | SCH |  |  |  | 40S |  |  | SCH |  | 10S
|  |  | OD NOZZLE |  |  |  | 21.3 |  |  | OD NOZZLE |  | 21.3
|  |  | THICKNESS |  |  |  | 2.77 | mm |  | THICKNESS |  | 2.11 | mm
|  |  | WEIGHT |  |  |  | 1.3 | kg/m |  | WEIGHT |  | 1.01 | kg/m
|  |  | 12 | (lookup for thickness column) | [5 empty] | 7
|  |  | 10 | (lookup for weight row) | [5 empty] | 10
|  |  | NOMINAL SIZE |  |  |  | OD | SCHEDULE
|  |  | DN | 1 | INCH | DN | mm | 5S | 10S | 10 | 20 | 30 | STD | 40S | 40 | 60 | XS | 80S | 80 | 100 | 120 | 140 | 160 | XXS
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
6 |  | 1/8 | 6 | 3 | 1/8 | 6 | 10.3 | - | 1.24 | - | - | - | 1.73 | 1.73 | 1.73 | - | 2.41 | 2.41 | 2.41 | - | - | - | - | -
8 | 6.5 | 1/4 |  | 4 |  |  |  | - | 0.28 | - | - | - | 0.37 | 0.36 | 0.37 | - | 0.47 | 0.48 | 0.47 | - | - | - | - | -
10 |  | 3/8 | 8 | 5 | 1/4 | 8 | 13.7 | - | 1.65 | - | - | - | 2.24 | 2.24 | 2.24 | - | 3.12 | 3.02 | 3.12 | - | - | - | - | -
15 | 8.5 | 1/2 |  | 6 |  |  |  | - | 0.51 | - | - | - | 0.63 | 0.64 | 0.63 | - | 0.8 | 0.82 | 0.8 | - | - | - | - | -
20 |  | 3/4 | 10 | 7 | 3/8 | 10 | 17.1 | - | 1.65 | - | - | - | 2.31 | 2.31 | 2.31 | - | 3.21 | 3.2 | 3.21 | - | - | - | - | -
25 | 10.5 | 1 |  | 8 |  |  |  | - | 0.64 | - | - | - | 0.84 | 0.86 | 0.84 | - | 1.1 | 1.12 | 1.1 | - | - | - | - | -
32 |  | 1 1/4 | 15 | 9 | 1/2 | 15 | 21.3 | 1.65 | 2.11 | - | - | - | 2.77 | 2.77 | 2.77 | - | 3.73 | 3.73 | 3.73 | - | - | - | 4.78 | 7.47
40 | 15.5 | 1 1/2 |  | 10 |  |  |  | 0.82 | 1.01 | - | - | - | 1.27 | 1.3 | 1.27 | - | 1.62 | 1.65 | 1.62 | - | - | - | 1.95 | 2.55
50 |  | 2 | 20 | 11 | 3/4 | 20 | 26.7 | 1.65 | 2.11 | - | - | - | 2.87 | 2.87 | 2.87 | - | 3.91 | 3.91 | 3.91 | - | - | - | 5.56 | 7.82
65 | 20.5 | 2 1/2 |  | 12 |  |  |  | 1.04 | 1.31 | - | - | - | 1.69 | 1.71 | 1.69 | - | 2.2 | 2.24 | 2.2 | - | - | - | 2.9 | 3.64
80 |  | 3 | 25 | 13 | 1 | 25 | 33.4 | 1.65 | 2.77 | - | - | - | 3.38 | 3.38 | 3.38 | - | 4.55 | 4.55 | 4.55 | - | - | - | 6.35 | 9.09
90 | 25.5 | 3 1/2 |  | 14 |  |  |  | 1.33 | 2.13 | - | - | - | 2.5 | 2.55 | 2.5 | - | 3.24 | 3.29 | 3.24 | - | - | - | 4.24 | 5.45
100 |  | 4 | 32 | 15 | 1 1/4 | 32 | 42.2 | 1.65 | 2.77 | - | - | - | 3.56 | 3.56 | 3.56 | - | 4.85 | 4.85 | 4.85 | - | - | - | 6.35 | 9.7
125 | 32.5 | 5 |  | 16 |  |  |  | 1.68 | 2.76 | - | - | - | 3.39 | 3.46 | 3.39 | - | 4.47 | 4.56 | 4.47 | - | - | - | 5.61 | 7.77
150 |  | 6 | 40 | 17 | 1 1/2 | 40 | 48.3 | 1.65 | 2.77 | - | - | - | 3.68 | 3.68 | 3.68 | - | 5.08 | 5.08 | 5.08 | - | - | - | 7.14 | 10.15
200 | 40.5 | 8 |  | 18 |  |  |  | 1.95 | 3.1 | - | - | - | 4.05 | 4.13 | 4.05 | - | 5.41 | 5.51 | 5.41 | - | - | - | 7.25 | 9.56
250 |  | 10 | 50 | 19 | 2 | 50 | 60.3 | 1.65 | 2.77 | - | - | - | 3.91 | 3.91 | 3.91 | - | 5.54 | 5.54 | 5.54 | - | - | - | 8.74 | 11.07
300 | 50.5 | 12 |  | 20 |  |  |  | 2.44 | 4.01 | - | - | - | 5.44 | 5.54 | 5.44 | - | 7.48 | 7.63 | 7.48 | - | - | - | 11.11 | 13.14
350 |  | 14 | 65 | 21 | 2 1/2 | 65 | 73 | 2.11 | 3.05 | - | - | - | 5.16 | 5.16 | 5.16 | - | 7.01 | 7.01 | 7.01 | - | - | - | 9.53 | 14.02
400 | 65.5 | 16 |  | 22 |  |  |  | 3.77 | 5.36 | - | - | - | 8.63 | 8.81 | 8.63 | - | 11.41 | 11.64 | 11.41 | - | - | - | 14.92 | 20.39
450 |  | 18 | 80 | 23 | 3 | 80 | 88.9 | 2.11 | 3.05 | - | - | - | 5.49 | 5.49 | 5.49 | - | 7.62 | 7.62 | 7.62 | - | - | - | 11.13 | 15.24
500 | 80.5 | 20 |  | 24 |  |  |  | 4.6 | 6.59 | - | - | - | 11.29 | 11.52 | 11.29 | - | 15.27 | 15.59 | 15.27 | - | - | - | 21.35 | 27.68
550 |  | 22 | 90 | 25 | 3 1/2 | 90 | 101.6 | 2.11 | 3.05 | - | - | - | 5.74 | 5.74 | 5.74 | - | 8.08 | 8.08 | 8.08 | - | - | - | - | -
600 | 90.5 | 24 |  | 26 |  |  |  | 5.29 | 7.55 | - | - | - | 13.57 | 13.84 | 13.57 | - | 18.63 | 19.01 | 18.63 | - | - | - | - | -
650 |  | 26 | 100 | 27 | 4 | 100 | 114.3 | 2.11 | 3.05 | - | - | - | 6.02 | 6.02 | 6.02 | - | 8.56 | 8.56 | 8.56 | - | 11.13 | - | 13.49 | 17.12
700 | 100.5 | 28 |  | 28 |  |  |  | 5.96 | 8.52 | - | - | - | 16.07 | 16.4 | 16.07 | - | 22.32 | 22.77 | 22.32 | - | 28.32 | - | 33.54 | 41.03
750 |  | 30 | 125 | 29 | 5 | 125 | 141.3 | 2.77 | 3.4 | - | - | - | 6.55 | 6.55 | 6.55 | - | 9.53 | 9.53 | 9.53 | - | 12.7 | - | 15.88 | 19.05
800 | 125.5 | 32 |  | 30 |  |  |  | 9.67 | 11.82 | - | - | - | 21.77 | 22.2 | 21.77 | - | 30.97 | 31.59 | 30.97 | - | 40.28 | - | 49.11 | 57.43
850 |  | 34 | 150 | 31 | 6 | 150 | 168.3 | 2.77 | 3.4 | - | - | - | 7.11 | 7.11 | 7.11 | - | 10.97 | 10.97 | 10.97 | - | 14.27 | - | 18.26 | 21.95
900 | 150.5 | 36 |  | 32 |  |  |  | 11.55 | 14.13 | - | - | - | 28.26 | 28.83 | 28.26 | - | 42.56 | 43.42 | 42.56 | - | 54.2 | - | 67.56 | 79.22
950 |  | 38 | 200 | 33 | 8 | 200 | 219.1 | 2.77 | 3.76 | - | 6.35 | 7.04 | 8.18 | 8.18 | 8.18 | 10.31 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 22.23
1000 | 200.5 | 40 |  | 34 |  |  |  | 15.09 | 20.37 | - | 33.31 | 36.81 | 42.55 | 43.39 | 42.55 | 53.08 | 64.64 | 65.95 | 64.64 | 75.92 | 90.44 | 100.92 | 111.27 | 107.92
1050 |  | 42 | 250 | 35 | 10 | 250 | 273.1 | 3.4 | 4.19 | - | 6.35 | 7.8 | 9.27 | 9.27 | 9.27 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 25.4
1100 | 250.5 | 44 |  | 36 |  |  |  | 23.08 | 28.34 | - | 41.77 | 51.03 | 60.31 | 61.52 | 60.31 | 81.55 | 81.55 | 83.19 | 96.01 | 114.75 | 133.06 | 155.15 | 172.33 | 155.15
1150 |  | 46 | 300 | 37 | 12 | 300 | 323.9 | 3.96 | 4.57 | - | 6.35 | 8.38 | 9.53 | 9.52 | 10.31 | 14.27 | 12.7 | 12.7 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 25.4
1200 | 300.5 | 48 |  | 38 |  |  |  | 31.89 | 36.73 | - | 49.73 | 65.2 | 73.88 | 75.32 | 79.73 | 108.96 | 97.46 | 99.43 | 132.08 | 159.91 | 186.75 | 208.14 | 238.76 | 186.97
|  |  | 350 | 39 | 14 | 350 | 355.6 | 3.96 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 11.13 | 15.09 | 12.7 | - | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | -
| 350.5 |  |  | 40 |  |  |  | 35.06 | 42.14 | 54.69 | 67.9 | 81.33 | 81.33 | - | 94.55 | 12.71 | 107.39 | - | 158.1 | 194.96 | 224.65 | 253.56 | 281.7 | -
|  |  | 400 | 41 | 16 | 400 | 406.4 | 4.19 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 12.7 | 16.66 | 12.7 | - | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | -
| 400.5 |  |  | 42 |  |  |  | 42.41 | 48.26 | 62.64 | 77.83 | 93.27 | 93.27 | - | 123.3 | 160.12 | 123.3 | - | 203.53 | 245.56 | 286.64 | 333.19 | 365.35 | -
|  |  | 450 | 43 | 18 | 450 | 457.2 | 4.19 | 4.78 | 6.35 | 7.92 | 11.13 | 9.53 | - | 14.27 | 19.05 | 12.7 | - | 23.88 | 29.36 | 34.93 | 39.67 | 45.34 | -
| 450.5 |  |  | 44 |  |  |  | 47.77 | 54.36 | 70.57 | 87.71 | 122.38 | 105.16 | - | 155.8 | 205.74 | 139.15 | - | 254.55 | 309.62 | 363.56 | 408.26 | 459.37 | -
|  |  | 500 | 45 | 20 | 500 | 508 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | 15.09 | 20.62 | 12.7 | - | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | -
| 500.5 |  |  | 46 |  |  |  | 60.46 | 70 | 78.55 | 117.15 | 155.12 | 117.15 | - | 173.42 | 247.83 | 155.12 | - | 311.17 | 381.53 | 441.49 | 508.11 | 564.81 | -
|  |  | 550 | 47 | 22 | 550 | 558.8 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | - | 22.23 | 12.7 | - | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | -
| 550.5 |  |  | 48 |  |  |  | 66.57 | 77.06 | 86.54 | 127.13 | 171.09 | 129.13 | - | - | 294.25 | 171.09 | - | 373.83 | 451.42 | 527.02 | 600.63 | 672.26 | -
|  |  | 600 | 49 | 24 | 600 | 609.8 | 5.54 | 6.35 | 6.35 | 9.53 | 14.27 | 9.53 | - | 17.48 | 24.61 | 12.7 | - | 30.96 | 39.89 | 46.02 | 52.37 | 59.54 | -
| 600.5 |  |  | 50 |  |  |  | 84.16 | 96.37 | 94.53 | 141.12 | 209.64 | 141.12 | - | 255.41 | 355.26 | 187.06 | - | 442.08 | 547.71 | 640.03 | 720.16 | 808.22 | -
|  |  | 650 | 51 | 26 | 650 | 660.4 | - | - | 7.92 | 12.7 | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 650.5 |  |  | 52 |  |  |  | - | - | 127.36 | 202.72 | - | 152.87 | - | - | - | 202.72 | - | - | - | - | - | - | -
|  |  | 700 | 53 | 28 | 700 | 711.2 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 700.5 |  |  | 54 |  |  |  | - | - | 137.32 | 218.69 | 271.21 | 164.87 | - | - | - | 218.69 | - | - | - | - | - | - | -
|  |  | 750 | 55 | 30 | 750 | 762 | 6.35 | 7.92 | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 750.5 |  |  | 56 |  |  |  | 120.72 | 150.36 | 147.28 | 234.67 | 292.18 | 176.84 | - | - | - | 234.67 | - | - | - | - | - | - | -
|  |  | 800 | 57 | 32 | 800 | 812.8 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 800.5 |  |  | 58 |  |  |  | - | - | 157.24 | 250.64 | 312.15 | 188.82 | - | 342.91 | - | 250.64 | - | - | - | - | - | - | -
|  |  | 850 | 59 | 34 | 850 | 863.6 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 850.5 |  |  | 60 |  |  |  | - | - | 167.2 | 266.61 | 332.12 | 200.31 | - | 364.9 | - | 266.61 | - | - | - | - | - | - | -
|  |  | 900 | 61 | 36 | 900 | 914.4 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 19.05 | - | 12.7 | - | - | - | - | - | - | -
| 900.5 |  |  | 62 |  |  |  | - | - | 176.96 | 282.27 | 351.7 | 212.56 | - | 420.4 | - | 282.27 | - | - | - | - | - | - | -
|  |  | 950 | 63 | 38 | 950 | 965.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 950.5 |  |  | 64 |  |  |  | - | - | - | - | - | 224.54 | - | - | - | 298.24 | - | - | - | - | - | - | -
|  |  | 1000 | 65 | 40 | 1000 | 1016 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1000.5 |  |  | 66 |  |  |  | - | - | - | - | - | 236.53 | - | - | - | 314.22 | - | - | - | - | - | - | -
|  |  | 1050 | 67 | 42 | 1050 | 1066.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1050.5 |  |  | 68 |  |  |  | - | - | - | - | - | 248.53 | - | - | - | 330.19 | - | - | - | - | - | - | -
|  |  | 1100 | 69 | 44 | 1100 | 1117.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1100.5 |  |  | 70 |  |  |  | - | - | - | - | - | 260.5 | - | - | - | 346.16 | - | - | - | - | - | - | -
|  |  | 1150 | 71 | 46 | 1150 | 1168.4 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1150.5 |  |  | 72 |  |  |  | - | - | - | - | - | 272.25 | - | - | - | 351.82 | - | - | - | - | - | - | -
|  |  | 1200 | 73 | 48 | 1200 | 1219.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1200.5 |  |  | 74 |  |  |  | - | - | - | - | - | 284.24 | - | - | - | 377.79 | - | - | - | - | - | - | -
Available for stainless steel
Available for carbon steel

## M2-20"
| NOZZLE NECK THICKNESS CALCULATION |  |  |  |  | (UG-45) |  |  |  |  | Page : | 10
| NECK THICKNESS OF |  |  | 20 | " | ( | DN | 500 | )
FOR M2
| Nozzle Dimension |  | : | 508 | mm O/D * | 6 | mm thk |  | (PLATE)
| Material |  | : | A240 TP304
From UG-45(a)
| Minimum required thickness | [12 empty] | MPATO PSI
[13 empty] | 0.00296 | 145.038
| t | = | PRo |  | + | C |  |  | P | = | 0.42931 | psi |  | 0.42931
|  |  | SE + 0.4P | [5 empty] | R | = | 10 | in
[9 empty] | S | = | 17100 | psi
|  | = | 0.00025106 | + | 0 |  |  |  | E | = | 1
[9 empty] | C | = | 0 | in
|  | = | 0.00025106 | in / | 0.0063769 | mm |  |  | t | = | 0.19685 | in
[9 empty] | tn | = | 0.23622 | in
| From UG-45(b)(1) |  | (SHELL THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.09375 | in / | 2.3813 | mm
| From UG-45(b)(1) |  | (END PLATE THICKNESS WHERE NOZZLE ATTACHED)
| t (shell) | = | 0.23622 | in / | 6 | mm
From UG-45(b)(4)
| Standard (STD) wall thk of |  |  | 20 | NB = | 0.216 | in
Min. thickness of STD wall thickness
| = | std wall thk - 12.5%std wall thk + C
| = | 0.189 | in / | 4.8006 | mm
Hence from UG-45(b)
| Smaller thickness = |  | 0.189 | in / | 4.8006 | mm
From UG-45(a)
| Required wall thickness = |  |  | 0.189 | in / | 4.8006 | mm
| Hence pipe of |  | 20 | NB | 6 | mm thk ( sch |  | 0 | ) is adequate
Checking for 12.5%
| 0.875 * | 6 | = | 5.25 | mm > | 4.8006 | mm ( sufficient)
Checking for weld size ( UW -16 )
|  | tc | = | not less than the smaller of 0.25 in or 0.7tmin
|  |  | = | 0.7 * 0.75 | or | 0.7 * tn |  | or | 0.7 * t |  | or | 0.25
|  |  | = | 0.525 | in | 0.16535 |  | in | 0.1378 |  | in | 0.25
| Therefore, throat must not be less than |  |  |  |  | 0.1378 |  | in / | 3.5 |  | mm
| If weld size is | 0.23622 | in / |  | 6 | mm
| Actual | tc | = | 0.7 * weld size
|  |  | = | 0.16535 | in / | 4.2 |  | mm | > | 3.5 |  | mm
| Hence, weld size |  | = | 0.23622 | in / | 6 |  | mm | is satisfactory
Strength calculations for attachment welds are not required for this detail which conforms to UW-16

## PIPEDATA-20"
|  |  | DN BASE | [6 empty] | INCH BASE
|  |  | SIZE |  | DN |  | 650 |  |  | SIZE | INCH | 20
[5 empty] | INCH |  | 26 |  |  |  | DN | 500
|  |  | SCH |  |  |  | 40S |  |  | SCH |  | 10S
|  |  | OD NOZZLE |  |  |  | 650 |  |  | OD NOZZLE |  | 508
|  |  | THICKNESS |  |  |  | - | mm |  | THICKNESS |  | 6 | mm
|  |  | WEIGHT |  |  |  | - | kg/m |  | WEIGHT |  | 70 | kg/m
|  |  | 12 | (lookup for thickness column) | [5 empty] | 7
|  |  | 52 | (lookup for weight row) | [5 empty] | 46
|  |  | NOMINAL SIZE |  |  |  | OD | SCHEDULE
|  |  | DN | 1 | INCH | DN | mm | 5S | 10S | 10 | 20 | 30 | STD | 40S | 40 | 60 | XS | 80S | 80 | 100 | 120 | 140 | 160 | XXS
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
6 |  | 1/8 | 6 | 3 | 1/8 | 6 | 10.3 | - | 1.24 | - | - | - | 1.73 | 1.73 | 1.73 | - | 2.41 | 2.41 | 2.41 | - | - | - | - | -
8 | 6.5 | 1/4 |  | 4 |  |  |  | - | 0.28 | - | - | - | 0.37 | 0.36 | 0.37 | - | 0.47 | 0.48 | 0.47 | - | - | - | - | -
10 |  | 3/8 | 8 | 5 | 1/4 | 8 | 13.7 | - | 1.65 | - | - | - | 2.24 | 2.24 | 2.24 | - | 3.12 | 3.02 | 3.12 | - | - | - | - | -
15 | 8.5 | 1/2 |  | 6 |  |  |  | - | 0.51 | - | - | - | 0.63 | 0.64 | 0.63 | - | 0.8 | 0.82 | 0.8 | - | - | - | - | -
20 |  | 3/4 | 10 | 7 | 3/8 | 10 | 17.1 | - | 1.65 | - | - | - | 2.31 | 2.31 | 2.31 | - | 3.21 | 3.2 | 3.21 | - | - | - | - | -
25 | 10.5 | 1 |  | 8 |  |  |  | - | 0.64 | - | - | - | 0.84 | 0.86 | 0.84 | - | 1.1 | 1.12 | 1.1 | - | - | - | - | -
32 |  | 1 1/4 | 15 | 9 | 1/2 | 15 | 21.3 | 1.65 | 2.11 | - | - | - | 2.77 | 2.77 | 2.77 | - | 3.73 | 3.73 | 3.73 | - | - | - | 4.78 | 7.47
40 | 15.5 | 1 1/2 |  | 10 |  |  |  | 0.82 | 1.01 | - | - | - | 1.27 | 1.3 | 1.27 | - | 1.62 | 1.65 | 1.62 | - | - | - | 1.95 | 2.55
50 |  | 2 | 20 | 11 | 3/4 | 20 | 26.7 | 1.65 | 2.11 | - | - | - | 2.87 | 2.87 | 2.87 | - | 3.91 | 3.91 | 3.91 | - | - | - | 5.56 | 7.82
65 | 20.5 | 2 1/2 |  | 12 |  |  |  | 1.04 | 1.31 | - | - | - | 1.69 | 1.71 | 1.69 | - | 2.2 | 2.24 | 2.2 | - | - | - | 2.9 | 3.64
80 |  | 3 | 25 | 13 | 1 | 25 | 33.4 | 1.65 | 2.77 | - | - | - | 3.38 | 3.38 | 3.38 | - | 4.55 | 4.55 | 4.55 | - | - | - | 6.35 | 9.09
90 | 25.5 | 3 1/2 |  | 14 |  |  |  | 1.33 | 2.13 | - | - | - | 2.5 | 2.55 | 2.5 | - | 3.24 | 3.29 | 3.24 | - | - | - | 4.24 | 5.45
100 |  | 4 | 32 | 15 | 1.25 | 32 | 42.2 | 1.65 | 2.77 | - | - | - | 3.56 | 3.56 | 3.56 | - | 4.85 | 4.85 | 4.85 | - | - | - | 6.35 | 9.7
125 | 32.5 | 5 |  | 16 |  |  |  | 1.68 | 2.76 | - | - | - | 3.39 | 3.46 | 3.39 | - | 4.47 | 4.56 | 4.47 | - | - | - | 5.61 | 7.77
150 |  | 6 | 40 | 17 | 1.5 | 40 | 48.3 | 1.65 | 2.77 | - | - | - | 3.68 | 3.68 | 3.68 | - | 5.08 | 5.08 | 5.08 | - | - | - | 7.14 | 10.15
200 | 40.5 | 8 |  | 18 |  |  |  | 1.95 | 3.1 | - | - | - | 4.05 | 4.13 | 4.05 | - | 5.41 | 5.51 | 5.41 | - | - | - | 7.25 | 9.56
250 |  | 10 | 50 | 19 | 2 | 50 | 60.3 | 1.65 | 2.77 | - | - | - | 3.91 | 3.91 | 3.91 | - | 5.54 | 5.54 | 5.54 | - | - | - | 8.74 | 11.07
300 | 50.5 | 12 |  | 20 |  |  |  | 2.44 | 4.01 | - | - | - | 5.44 | 5.54 | 5.44 | - | 7.48 | 7.63 | 7.48 | - | - | - | 11.11 | 13.14
350 |  | 14 | 65 | 21 | 2.5 | 65 | 73 | 2.11 | 3.05 | - | - | - | 5.16 | 5.16 | 5.16 | - | 7.01 | 7.01 | 7.01 | - | - | - | 9.53 | 14.02
400 | 65.5 | 16 |  | 22 |  |  |  | 3.77 | 5.36 | - | - | - | 8.63 | 8.81 | 8.63 | - | 11.41 | 11.64 | 11.41 | - | - | - | 14.92 | 20.39
450 |  | 18 | 80 | 23 | 3 | 80 | 88.9 | 2.11 | 3.05 | - | - | - | 5.49 | 5.49 | 5.49 | - | 7.62 | 7.62 | 7.62 | - | - | - | 11.13 | 15.24
500 | 80.5 | 20 |  | 24 |  |  |  | 4.6 | 6.59 | - | - | - | 11.29 | 11.52 | 11.29 | - | 15.27 | 15.59 | 15.27 | - | - | - | 21.35 | 27.68
550 |  | 22 | 90 | 25 | 3.5 | 90 | 101.6 | 2.11 | 3.05 | - | - | - | 5.74 | 5.74 | 5.74 | - | 8.08 | 8.08 | 8.08 | - | - | - | - | -
600 | 90.5 | 24 |  | 26 |  |  |  | 5.29 | 7.55 | - | - | - | 13.57 | 13.84 | 13.57 | - | 18.63 | 19.01 | 18.63 | - | - | - | - | -
650 |  | 26 | 100 | 27 | 4 | 100 | 114.3 | 2.11 | 3.05 | - | - | - | 6.02 | 6.02 | 6.02 | - | 8.56 | 8.56 | 8.56 | - | 11.13 | - | 13.49 | 17.12
700 | 100.5 | 28 |  | 28 |  |  |  | 5.96 | 8.52 | - | - | - | 16.07 | 16.4 | 16.07 | - | 22.32 | 22.77 | 22.32 | - | 28.32 | - | 33.54 | 41.03
750 |  | 30 | 125 | 29 | 5 | 125 | 141.3 | 2.77 | 3.4 | - | - | - | 6.55 | 6.55 | 6.55 | - | 9.53 | 9.53 | 9.53 | - | 12.7 | - | 15.88 | 19.05
800 | 125.5 | 32 |  | 30 |  |  |  | 9.67 | 11.82 | - | - | - | 21.77 | 22.2 | 21.77 | - | 30.97 | 31.59 | 30.97 | - | 40.28 | - | 49.11 | 57.43
850 |  | 34 | 150 | 31 | 6 | 150 | 168.3 | 2.77 | 3.4 | - | - | - | 7.11 | 7.11 | 7.11 | - | 10.97 | 10.97 | 10.97 | - | 14.27 | - | 18.26 | 21.95
900 | 150.5 | 36 |  | 32 |  |  |  | 11.55 | 14.13 | - | - | - | 28.26 | 28.83 | 28.26 | - | 42.56 | 43.42 | 42.56 | - | 54.2 | - | 67.56 | 79.22
950 |  | 38 | 200 | 33 | 8 | 200 | 219.1 | 2.77 | 3.76 | - | 6.35 | 7.04 | 8.18 | 8.18 | 8.18 | 10.31 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 20.62 | 23.01 | 22.23
1000 | 200.5 | 40 |  | 34 |  |  |  | 15.09 | 20.37 | - | 33.31 | 36.81 | 42.55 | 43.39 | 42.55 | 53.08 | 64.64 | 65.95 | 64.64 | 75.92 | 90.44 | 100.92 | 111.27 | 107.92
1050 |  | 42 | 250 | 35 | 10 | 250 | 273.1 | 3.4 | 4.19 | - | 6.35 | 7.8 | 9.27 | 9.27 | 9.27 | 12.7 | 12.7 | 12.7 | 15.09 | 18.26 | 21.44 | 25.4 | 28.58 | 25.4
1100 | 250.5 | 44 |  | 36 |  |  |  | 23.08 | 28.34 | - | 41.77 | 51.03 | 60.31 | 61.52 | 60.31 | 81.55 | 81.55 | 83.19 | 96.01 | 114.75 | 133.06 | 155.15 | 172.33 | 155.15
1150 |  | 46 | 300 | 37 | 12 | 300 | 323.9 | 3.96 | 4.57 | - | 6.35 | 8.38 | 9.53 | 9.52 | 10.31 | 14.27 | 12.7 | 12.7 | 17.48 | 21.44 | 25.4 | 28.58 | 33.32 | 25.4
1200 | 300.5 | 48 |  | 38 |  |  |  | 31.89 | 36.73 | - | 49.73 | 65.2 | 73.88 | 75.32 | 79.73 | 108.96 | 97.46 | 99.43 | 132.08 | 159.91 | 186.75 | 208.14 | 238.76 | 186.97
|  |  | 350 | 39 | 14 | 350 | 355.6 | 3.96 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 11.13 | 15.09 | 12.7 | - | 19.05 | 23.83 | 27.79 | 31.75 | 35.71 | -
| 350.5 |  |  | 40 |  |  |  | 35.06 | 42.14 | 54.69 | 67.9 | 81.33 | 81.33 | - | 94.55 | 12.71 | 107.39 | - | 158.1 | 194.96 | 224.65 | 253.56 | 281.7 | -
|  |  | 400 | 41 | 16 | 400 | 406.4 | 4.19 | 4.78 | 6.35 | 7.92 | 9.53 | 9.53 | - | 12.7 | 16.66 | 12.7 | - | 21.44 | 26.19 | 30.96 | 36.53 | 40.49 | -
| 400.5 |  |  | 42 |  |  |  | 42.41 | 48.26 | 62.64 | 77.83 | 93.27 | 93.27 | - | 123.3 | 160.12 | 123.3 | - | 203.53 | 245.56 | 286.64 | 333.19 | 365.35 | -
|  |  | 450 | 43 | 18 | 450 | 457.2 | 4.19 | 4.78 | 6.35 | 7.92 | 11.13 | 9.53 | - | 14.27 | 19.05 | 12.7 | - | 23.88 | 29.36 | 34.93 | 39.67 | 45.34 | -
| 450.5 |  |  | 44 |  |  |  | 47.77 | 54.36 | 70.57 | 87.71 | 122.38 | 105.16 | - | 155.8 | 205.74 | 139.15 | - | 254.55 | 309.62 | 363.56 | 408.26 | 459.37 | -
|  |  | 500 | 45 | 20 | 500 | 508 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | 15.09 | 20.62 | 12.7 | - | 26.19 | 32.54 | 38.1 | 44.45 | 50.01 | -
| 500.5 |  |  | 46 |  |  |  | 60.46 | 70 | 78.55 | 117.15 | 155.12 | 117.15 | - | 173.42 | 247.83 | 155.12 | - | 311.17 | 381.53 | 441.49 | 508.11 | 564.81 | -
|  |  | 550 | 47 | 22 | 550 | 558.8 | 4.78 | 5.54 | 6.35 | 9.53 | 12.7 | 9.53 | - | - | 22.23 | 12.7 | - | 28.58 | 34.93 | 41.28 | 47.63 | 53.98 | -
| 550.5 |  |  | 48 |  |  |  | 66.57 | 77.06 | 86.54 | 127.13 | 171.09 | 129.13 | - | - | 294.25 | 171.09 | - | 373.83 | 451.42 | 527.02 | 600.63 | 672.26 | -
|  |  | 600 | 49 | 24 | 600 | 609.8 | 5.54 | 6.35 | 6.35 | 9.53 | 14.27 | 9.53 | - | 17.48 | 24.61 | 12.7 | - | 30.96 | 39.89 | 46.02 | 52.37 | 59.54 | -
| 600.5 |  |  | 50 |  |  |  | 84.16 | 96.37 | 94.53 | 141.12 | 209.64 | 141.12 | - | 255.41 | 355.26 | 187.06 | - | 442.08 | 547.71 | 640.03 | 720.16 | 808.22 | -
|  |  | 650 | 51 | 26 | 650 | 650 | - | - | 7.92 | 12.7 | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 650.5 |  |  | 52 |  |  |  | - | - | 127.36 | 202.72 | - | 152.87 | - | - | - | 202.72 | - | - | - | - | - | - | -
|  |  | 700 | 53 | 28 | 700 | 711.2 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 700.5 |  |  | 54 |  |  |  | - | - | 137.32 | 218.69 | 271.21 | 164.87 | - | - | - | 218.69 | - | - | - | - | - | - | -
|  |  | 750 | 55 | 30 | 750 | 762 | 6.35 | 7.92 | 7.92 | 12.7 | 15.88 | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 750.5 |  |  | 56 |  |  |  | 120.72 | 150.36 | 147.28 | 234.67 | 292.18 | 176.84 | - | - | - | 234.67 | - | - | - | - | - | - | -
|  |  | 800 | 57 | 32 | 800 | 812.8 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 800.5 |  |  | 58 |  |  |  | - | - | 157.24 | 250.64 | 312.15 | 188.82 | - | 342.91 | - | 250.64 | - | - | - | - | - | - | -
|  |  | 850 | 59 | 34 | 850 | 863.6 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 17.48 | - | 12.7 | - | - | - | - | - | - | -
| 850.5 |  |  | 60 |  |  |  | - | - | 167.2 | 266.61 | 332.12 | 200.31 | - | 364.9 | - | 266.61 | - | - | - | - | - | - | -
|  |  | 900 | 61 | 36 | 900 | 914.4 | - | - | 7.92 | 12.7 | 15.88 | 9.53 | - | 19.05 | - | 12.7 | - | - | - | - | - | - | -
| 900.5 |  |  | 62 |  |  |  | - | - | 176.96 | 282.27 | 351.7 | 212.56 | - | 420.4 | - | 282.27 | - | - | - | - | - | - | -
|  |  | 950 | 63 | 38 | 950 | 965.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 950.5 |  |  | 64 |  |  |  | - | - | - | - | - | 224.54 | - | - | - | 298.24 | - | - | - | - | - | - | -
|  |  | 1000 | 65 | 40 | 1000 | 1016 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1000.5 |  |  | 66 |  |  |  | - | - | - | - | - | 236.53 | - | - | - | 314.22 | - | - | - | - | - | - | -
|  |  | 1050 | 67 | 42 | 1050 | 1066.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1050.5 |  |  | 68 |  |  |  | - | - | - | - | - | 248.53 | - | - | - | 330.19 | - | - | - | - | - | - | -
|  |  | 1100 | 69 | 44 | 1100 | 1117.8 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1100.5 |  |  | 70 |  |  |  | - | - | - | - | - | 260.5 | - | - | - | 346.16 | - | - | - | - | - | - | -
|  |  | 1150 | 71 | 46 | 1150 | 1168.4 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1150.5 |  |  | 72 |  |  |  | - | - | - | - | - | 272.25 | - | - | - | 351.82 | - | - | - | - | - | - | -
|  |  | 1200 | 73 | 48 | 1200 | 1219.2 | - | - | - | - | - | 9.53 | - | - | - | 12.7 | - | - | - | - | - | - | -
| 1200.5 |  |  | 74 |  |  |  | - | - | - | - | - | 284.24 | - | - | - | 377.79 | - | - | - | - | - | - | -
Available for stainless steel
Available for carbon steel

## _SSC (hidden)
REMOVED | {"ButtonStyle":0,"Name":"","HideSscPoweredlogo":false,"CopyProtect":{"IsEnabled":false,"DomainName":""},"Theme":{"BgColor":"#FFFFFFFF","BgImage":"","InputBorderStyle":2},"Layout":0,"SmartphoneSettings":{"ViewportLock":true,"UseOldViewEngine":false,"EnableZoom":false,"EnableSwipe":false,"HideToolbar":false,"CheckboxFlavor":1},"SmartphoneTheme":0,"InputDetection":0,"Toolbar":{"Position":1,"IsSubmit":true,"IsPrint":true,"IsPrintAll":false,"IsReset":true,"IsUpdate":true},"AspnetConfig":{"BrowseUrl":"http://localhost/ssc","FileExtension":0},"ConfigureSubmit":{"IsShowCaptcha":false,"IsUseSscWebServer":true,"ReceiverCode":"","IsFreeService":false,"IsAdvanceService":false,"IsDemonstrationService":true,"AfterSuccessfulSubmit":"","AfterFailSubmit":"","AfterCancelWizard":"","IsUseOwnWebServer":false,"OwnWebServerURL":"","OwnWebServerTarget":"","SubmitTarget":0},"Flavor":-1,"Edition":0,"IgnoreBgInputCell":false} | {"Captcha":{"Heading":"Enter the number displayed below.","Message":"This is to verify that you are a human visitor, to prevent automated form submissions.","OkButton":"OK","CancelButton":"Cancel","ErrorMessage":"Your answer is incorrect, please try again."},"RequiredField":{"ErrorMessage":"The fields with the red border are required.","OkButton":"OK","DDLDefaultRequiredText":"Please Select"},"WizardButton":{"Next":"Next","Previous":"Previous","Cancel":"Cancel","Finish":"Finish"},"ToolbarButton":{"Submit":"Submit","Print":"Print","PrintAll":"Print All","Reset":"Reset","Update":"Update","Back":"Back"},"BrowserAndLocation":{"Browsers":[],"ConversionPath":"C:\\Users\\nasrul\\Documents\\SpreadsheetConverter"},"AdvancedSettingsModels":[],"Dropbox":{"AccessToken":"","AccessSecret":""},"SpreadsheetServer":{"Username":"","Password":"","ServerUrl":""},"ConfigureSubmitDefault":{"Email":""}}
REMOVED
{"IsHide":true,"SheetId":3,"Name":"Sheet1","HiddenRow":3,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":4,"Name":"TANK DESIGN","HiddenRow":4,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":5,"Name":"4\"","HiddenRow":5,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":6,"Name":"NOMINAL PIPE LOOK UP","HiddenRow":6,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
REMOVED
{"IsHide":false,"SheetId":8,"Name":"cONTENT (2)","HiddenRow":8,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}
{"IsHide":true,"SheetId":9,"Name":"WATER_SS_TANK (2)","HiddenRow":9,"VisibleRange":"","SheetTheme":{"TabColor":"","BodyColor":"","BodyImage":""}}